## Instructions & Formulae
Pole & Guy Loading: Design Criteria: This defines the Loading and Pole input data for the design. Input in this section includes the Loading Zone, Construction Grade, Pole material and Maximum Fiber Stress Pole Data: The calculated pole data required many of the subsequent calculations. Transverse Wind Loading: Loading calculation on tangent poles based on cross wind loading on the pole and conductors. Maximum Unguyed Span at Line Angle: Calculation of maximum span for a given angle without guying. This is based on the maximum moment that the pole can withstand at the ground line. Insulator Swing: Calculation of the maximum line angle limited by reduced clearance from insulator swing. Vertical Loading: Calculation of the maximum vertical loading allowed on a pole without buckling based on guy lead. Miscellaneous Transmission Guy: Calculation of guying requirements for poles under design load in various configurations.
Metal Pole Deflection
THIS PROGRAM IS STILL IN DEVELOPMENT.
The Transverse Loading Deflection calculation is based the formulae presented in tables B1 and B4 of the AASHTO STANDARD SPECIFICATIONS FOR STRUCTURAL SUPPORTS FOR HIGHWAY SIGNS, LUMINAIRES, AND TRAFFIC SIGNALS, Appendix B: Design Aids as follows:
where:
da = diameter at free end db = diameter at fixed end E = modulus of elasticity Ia = moment of inertia of cross-section at free end of beam L = length M = moment applied at free end of beam P = horizontal load applied at free end of beam w = uniformly distributed load applied along the beam length ymax = deflection at free end of beam θmax = slope at free end of beam (rad)
𝑦_𝑚𝑎𝑥=(𝑃𝐿^3)/(3𝐸𝐼_𝑎 (𝑑_𝑏/𝑑_𝑎 )^3 )
𝜃_𝑚𝑎𝑥=(𝑃𝐿^2)/(2.068𝐸𝐼_𝑎 (𝑑_𝑏/𝑑_𝑎 )^2.497 )

## Pole & Guy Loading
| Project Description: | Double Circuit 46kV Post with 636AAC/954AAC
Desigh Criteria | NESC Loading Zone | Medium | (Heavy, Medium or Light)
| Wind, psf | 4
| Radial Ice, radius in inches | 0.25
| NESC Construction Grade | B | Vertical Loads | Transverse Wind | Transverse Wire Tension | Longitudinal Loads In General | Longitudinal Loads At Deadends | Longitudinal Loads At Deadends (for guys)
| NESC 253-1 Overload Factor |  | 1.5 | 2.5 | 1.65 | 1.1 | 1.65 | 1.65
|  |  | Metal and Prestressed-Concrete Structures | Wood and Reinforced-Concrete Structures | Support Hardware | Guy Wire | Guy Anchor and Foundation
| NESC 261-1 Strength Factor (SF) | Wood | 1 | 0.65 | 1 | 0.9 | 1
| Maximum Fiber Stress | 8000
Pole Data | Pole Height | 50 | 55 | 60 | 65 | 70 | 75 | 80 | 85 | 90 | 95 | 100 | 105
Pole Class | bar: 8000 50 to 8000 105
| Diameter 6' from Butt of Pole (in) | 15.1197 | 15.7563 | 16.2338 | 16.7113 | 17.1887 | 17.6662 | 18.1437 | 18.6211 | 18.9394 | 19.4169 | 19.7352 | 20.0535
| Diameter at Top of Pole (in) | 9.231 | 9.231 | 9.231 | 9.231 | 9.231 | 9.231 | 9.231 | 9.231 | 9.231 | 9.231 | 9.231 | 9.231
| Diameter at Groundline (in) | 14.9859 | 15.5566 | 15.9744 | 16.3943 | 16.8157 | 17.2383 | 17.6619 | 18.0862 | 18.3616 | 18.7874 | 19.0647 | 19.343
| Section Modulus at Groundline (in3) | 330.4053 | 369.609 | 400.1998 | 432.5927 | 466.8161 | 502.9041 | 540.8937 | 580.8249 | 607.7545 | 651.0322 | 680.2866 | 710.5067
| Ultimate Resisting Moment (ft-lbs) | 220270.2277 | 246406.0251 | 266799.868 | 288395.1137 | 311210.7625 | 335269.3671 | 360595.8242 | 387216.6272 | 405169.6934 | 434021.4562 | 453524.3828 | 473671.1307
| Allowable Loading w/SF (ft-lbs) | 143175.648 | 160163.9163 | 173419.9142 | 187456.8239 | 202286.9956 | 217925.0886 | 234387.2857 | 251690.8077 | 263360.3007 | 282113.9465 | 294790.8488 | 307886.235
Transverse Wind Loading | Moment at the Ground due to Wind on the Pole (ft-lbs) | 4975.2217 | 6214.1062 | 7572.8306 | 9089.1496 | 10768.8639 | 12617.7741 | 14641.6812 | 16846.3862 | 19133.8942 | 21705.7167 | 24346.8926 | 27165.085
| Allowable Loading Less Moment due to Wind on Pole (ft-lbs) | 138200.4263 | 153949.8101 | 165847.0836 | 178367.6743 | 191518.1317 | 205307.3145 | 219745.6045 | 234844.4215 | 244226.4065 | 260408.2299 | 270443.9562 | 280721.1499
| Total Conductor Loading for 1ft. Span w/ OLF (ft-lbs) | 270.5296 | 310.3508 | 350.1721 | 389.9933 | 429.8146 | 469.6358 | 509.4571 | 549.2783 | 589.0996 | 628.9208 | 668.7421 | 708.5633
| Maximum Span Limited by Transverse Wind Load (feet) | 510.8514 | 496.0509 | 473.6159 | 457.3608 | 445.5831 | 437.1628 | 431.3329 | 427.5509 | 414.5758 | 414.0557 | 404.407 | 396.1836
Max Unguyed Span @ Line Angle | Line Angle (degrees) | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
| Total Tension due to Conductor Angle | 330.7741 | 330.7741 | 330.7741 | 330.7741 | 330.7741 | 330.7741 | 330.7741 | 330.7741 | 330.7741 | 330.7741 | 330.7741 | 330.7741
| Total Moment at Ground due to Conductor Angular Tensions w/ OLF (ft-lbs) | 19353.6019 | 21809.5994 | 24265.597 | 26721.5945 | 29177.5921 | 31633.5896 | 34089.5872 | 36545.5847 | 39001.5823 | 41457.5798 | 43913.5773 | 46369.5749
| Tension at Top of Pole (ft-lbs) | 450.0838 | 459.1495 | 466.6461 | 472.9486 | 478.3212 | 482.9556 | 486.9941 | 490.5448 | 493.6909 | 496.498 | 499.0179 | 501.2927
| Deflection at Top of Pole (Inches) | 7.509 | 9.2305 | 11.3672 | 13.6714 | 16.1248 | 18.7102 | 21.411 | 24.2122 | 27.7677 | 30.7827 | 34.658 | 38.7151
| Deflection Angle Slope (Degrees) | 1.5434 | 1.7501 | 1.9951 | 2.2374 | 2.4757 | 2.7089 | 2.9362 | 3.1573 | 3.4407 | 3.6506 | 3.9289 | 4.2058
| Total Conductor Loading for 1ft. Span @ Line Angle w/ OLF (lbs) | 270.5064 | 310.3242 | 350.1421 | 389.9599 | 429.7778 | 469.5956 | 509.4134 | 549.2313 | 589.0491 | 628.867 | 668.6848 | 708.5026
| Max Span at angle (feet) | 439.3494 | 425.8134 | 404.3544 | 388.8761 | 377.7314 | 369.8368 | 364.4506 | 361.048 | 348.4002 | 348.1669 | 338.77 | 330.7702
Insulator Swing | No. of Insulators in String | 8000 50: 0
| Weight of Insulator String @ 13.5lbs/insulator (lbs) | 8000 50: 0
| Additional Weight (lbs.) | 8000 50: 0
| Conductor Tension @30° Initial (lbs) | 8000 50: 1660
| Wind Span (feet) | 8000 50: 234
| Critical Swing Angle (degrees) | 8000 50: 48
| Conductor Swing @ Line Angle, Max Span & No Wind (degrees) | 8000 50: 11.7355
| Conductor Swing @ Line Angle & Max Span w/Wind (degrees) | 8000 50: 32.0805
| Min Weight Span @ Line Angle, Critical Swing Angle & Wind Span (feet) | 8000 50: 132.0688
Vertical Loading | E (modulus of elasticity psi) | 8000 50: 1800000
| Overload Factor | 8000 50: 1.5
| Ku | 8000 50: 0.7; 8000 55: For running angle or multiple deadends Ku=0.7; for single deadend Ku=2
| Distance from Top of Pole to Bottom Guy (ft) | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5
| Area at Critical Point (in2) | 137.8021 | 150.1197 | 160.3477 | 170.7812 | 181.4397 | 192.3372 | 203.4839 | 214.8875 | 223.23 | 235.0491 | 243.6153 | 252.2611
| Critical Buckling Load Pcr (lbs) | 667044.5911 | 791624.0432 | 903168.4933 | 1024526.6899 | 1156399.4352 | 1299480.6744 | 1454465.4494 | 1622054.9563 | 1750444.4871 | 1940709.1671 | 2084742.599 | 2235341.0623
| Moment on Pole at the Ground Line due to Wind (ft-lbs) | 4975.2217 | 6214.1062 | 7572.8306 | 9089.1496 | 10768.8639 | 12617.7741 | 14641.6812 | 16846.3862 | 19133.8942 | 21705.7167 | 24346.8926 | 27165.085
| Height of lowest Transmission Guy (ft) | 23 | 27.5 | 32 | 36.5 | 41 | 45.5 | 50 | 54.5 | 59 | 63.5 | 68 | 72.5
|  | 131.3808 | 135.0911 | 137.0087 | 139.1185 | 141.3825 | 143.7737 | 146.2725 | 148.8645 | 149.9032 | 152.6697 | 153.9075 | 155.2373
| Using Dist Calc | 435833.6804 | 322329.8478 | 244854.8164 | 194042.4878 | 158831.398 | 133367.1158 | 114313.6707 | 99655.6118 | 86224.4283 | 77209.5555 | 68424.8799 | 61239.1113
| da | 11.9077 | 11.8944 | 11.8246 | 11.7667 | 11.7178 | 11.676 | 11.6398 | 11.6082 | 11.5425 | 11.52 | 11.4659 | 11.4174
| dg | 14.9859 | 15.5566 | 15.9744 | 16.3943 | 16.8157 | 17.2383 | 17.6619 | 18.0862 | 18.3616 | 18.7874 | 19.0647 | 19.343
| IA | 986.9134 | 982.5156 | 959.6637 | 940.99 | 925.4472 | 912.3104 | 901.062 | 891.3229 | 871.3103 | 864.5165 | 848.412 | 834.1273
| Pcr | 364538.4355 | 274174.7846 | 211011.2497 | 169156.1008 | 139872.865 | 118504.1029 | 102378.0264 | 89870.2913 | 78144.0638 | 70350.7838 | 62580.8739 | 56192.7614
| Allowable Vertical Load w/SF | 236949.9831 | 178213.61 | 137157.3123 | 109951.4655 | 90917.3623 | 77027.6669 | 66545.7172 | 58415.6894 | 50793.6415 | 45728.0095 | 40677.5681 | 36525.2949
| Attachment Height | 23.5 | 28 | 32.5 | 37 | 41.5 | 46 | 50.5 | 55 | 59.5 | 64 | 68.5 | 73
| Wind Force at Guy Attachment | 211.7116 | 221.9324 | 233.0102 | 245.6527 | 259.4907 | 274.2994 | 289.9343 | 306.2979 | 321.5781 | 339.1518 | 355.4291 | 372.1245
| Total Tension and Wind | 25270 | 25270 | 25270 | 25270 | 25270 | 25270 | 25270 | 25270 | 25270 | 25270 | 25270 | 25270
| Additional Load | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Overload Factor | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65 | 1.65
| Tension with Overload | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5
| Vertical Component based on 1:1 lead | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5 | 41695.5
| Vertical Component based on 3:2 lead | 62543.25 | 62543.25 | 62543.25 | 62543.25 | 62543.25 | 62543.25 | 62543.25 | 62543.25 | 62543.25 | 62543.25 | 62543.25 | 62543.25
| Vertical Component based on 2:1 lead | 83391 | 83391 | 83391 | 83391 | 83391 | 83391 | 83391 | 83391 | 83391 | 83391 | 83391 | 83391
Miscellaneous Transmission Guying
| Transmission Loading | 8000 50: 13300
| Number of Guys | 8000 50: 2
| Guy Strand Rated Strength | 8000 50: 16000
| Table 261-1A Strength Factor | 8000 50: 0.9
| Guy Strand Allowable Strength | 8000 50: 14400
| Anchor Rated Strength | 8000 50: 23000
| Minimum Guy Lead Limited by Guy | 8000 50: 1.92:1
| Minimum Guy Lead Limited by Anchor | 8000 50: 3.5:1
12.925
| Line Angle | 8000 50: 30
| Ruling Span | 8000 50: 228
| Transverse Wind on Conductors | 8000 50: 779.5446
| Tension due to Wind on Pole (@90% out of ground) | 8000 50: 128.5587
| Conductor Tension | 8000 50: 6884.5866
| Transverse Wind on Conductors OLF from 253-1 | 8000 50: 2.5
| Tansverse Wire tension OLF for 253-1 | 8000 50: 1.65
| Total Tension from Wire & Wind w/OLF | 8000 50: 13629.8262
| Guy Strand Rated Strength | 8000 50: 16000
| Table 261-1A Strength Factor | 8000 50: 0.9
| Guy Strand Allowable Strength | 8000 50: 14400
| Anchor Rated Strength | 8000 50: 23000
| Number of Guys | 8000 50: 4; 8000 55: 3; 8000 60: 2; 8000 65: 1
| Minimum Guy Lead Limited by Guy | 8000 50: 4.11:1; 8000 55: 3.01:1; 8000 60: 1.86:1; 8000 65: 0.34:1
| Minimum Guy Lead Limited by Anchor | 8000 50: 6.68:1; 8000 55: 4.96:1; 8000 60: 1.36:1; 8000 65: #NUM!
Miscellaneous Distrubution Guying
| Distribution Loading | 8000 50: 11970
| Number of Guys | 8000 50: 2
| Guy Strand Rated Strength | 8000 50: 16000
| Table 261-1A Strength Factor | 8000 50: 0.9
| Guy Strand Allowable Strength | 8000 50: 14400
| Anchor Rated Strength | 8000 50: 23000
| Minimum Guy Lead Limited by Guy | 8000 50: 2.19:1
| Minimum Guy Lead Limited by Anchor | 8000 50: 5.66:1
2.475
| Line Angle | 8000 50: 30
| Ruling Span | 8000 50: 228
| Transverse Wind on Conductors | 8000 50: 0
| Tension due to Wind on Pole (@90% out of ground) | 8000 50: 17236.2943
| Conductor Tension | 8000 50: 6196.1279
| Transverse Wind on Conductors OLF from 253-1 | 8000 50: 2.5
| Tansverse Wire tension OLF for 253-1 | 8000 50: 1.65
| Total Tension from Wire & Wind w/OLF | 8000 50: 53314.347
| Guy Strand Rated Strength | 8000 50: 16000
| Table 261-1A Strength Factor | 8000 50: 0.9
| Guy Strand Allowable Strength | 8000 50: 14400
| Anchor Rated Strength | 8000 50: 23000
| Number of Guys | 8000 50: 4; 8000 55: 3; 8000 60: 2; 8000 65: 1
| Minimum Guy Lead Limited by Guy | 8000 50: 0.41:1; 8000 55: #NUM!; 8000 60: #NUM!; 8000 65: #NUM!
| Minimum Guy Lead Limited by Anchor | 8000 50: 1.41:1; 8000 55: 0.82:1; 8000 60: #NUM!; 8000 65: #NUM!

## Construction
| Transmission |  |  |  | Transmission Ckt 2 |  |  | Distribution Underbuild Ckt 1 |  |  |  | Distribution UB Ckt 2
| Static | Phase | Phase | Phase | Phase | Phase | Phase | Phase | Phase | Phase | Neutral | Phase | Phase | Phase
Conductor Code Word (from Conductor tab) | 3/8" hss | magnolia | magnolia | magnolia | magnolia | magnolia | magnolia
Conductor Desc | High Strength 3 OHGW | 954 37 AAC | 954 37 AAC | 954 37 AAC | 954 37 AAC | 954 37 AAC | 954 37 AAC
Diameter | 0.375 | 1.124 | 1.124 | 1.124 | 1.124 | 1.124 | 1.124 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Diameter of Ice | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
Wind in PSF | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
Design Tension | 1000 | 4100 | 4100 | 4100 |  | 0 | 0 | 3490 | 3490 | 3490 | 1500 |  | 0 | 0
% of Ultimate Strength | 11.96% | 25% | 25% | 25% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Sag at Ruling Span | 7 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
Ground Clearance | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 18.5 | 18.5 | 18.5 | 15.5 |  | 0 | 0
Total Horizontal Force per Foot in lbs. | 0.29167 | 0.54133 | 0.54133 | 0.54133 | 0.54133 | 0.54133 | 0.54133 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Weight per Foot of Conductor in lbs. | 0.22 | 0.894 | 0.894 | 0.894 | 0.894 | 0.894 | 0.894 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Distance from Top of Pole in ft. | 0.5 | 7.5 | 13.5 | 19.5 | 7.5 | 13.5 | 19.5 | 1 | 1 | 1 | 9 | 5 | 5 | 5
Moment Referenced to Top of Pole | 0.14583 | 4.06 | 7.308 | 10.556 | 4.06 | 7.308 | 10.556 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Conductor Tension Referenced to Top of Pole | 500 | 30750 | 55350 | 79950 | 0 | 0 | 0 | 3490 | 3490 | 3490 | 13500 | 0 | 0 | 0
Pole Height Required | 45 | 55 | 60 | 65 | 55 | 60 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Minimum Pole Height | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Moment at the Pole Top due to Conductor Tension | 500 | 30750 | 55350 | 79950 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Metal Pole Deflection
Calculation of Pole Deflection for Metal Poles
Pole Hgt | 65 | ft.
Class | h1
Pole Mfgr | McWane | McWane, Tapp or Union
Top Dia | 8.7 | in.
Base Dia | 19.6 | in.
Wall Thickness | 0.22 | in.
Shape | Round
Line Angle | 1.5 | deg.
ymax (maximum horizontal deflection at free end of beam) | 9.5132 | in.
From: AASHTO STANDARD SPECIFICATIONS FOR STRUCTURAL SUPPORTS FOR HIGHWAY SIGNS, LUMINAIRES, AND TRAFFIC SIGNALS, Appendix B: Design Aids
Where:
C = cross-sectional constant defined per Table B-1 (see ref) | 3.14
E = modulus of elasticity | 13400000
L = length of the beam (from ground line to top of pole) | 56.5 | ft.
RA = radius measured to mid-thickness of wall at free end | 8.59 | in.
RB = radius measured to mid-thickness of wall at fixed end | 18.0646 | in.
t = wall thickness | 0.22 | in.
W = load | 472.9486 | lbs.
McWane | 13400000
Tapp | 29000000
Union | 29000000
Pole Hgt | Class
65 | h1

## Wood Poles
Class Chart for Douglas Fir and Yellow Southern Pine Poles
Class |  | H2 | H1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 9 | 10 | H2 | H1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 9 | 10 |  | H2 | H1 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 9 | 10
Minimum Circumference at top (in) |  | 31 | 29 | 27 | 25 | 23 | 21 | 19 | 17 | 15 | 15 | 12 | [12 empty] | 4.9338 | 4.6155 | 4.2972 | 3.9789 | 3.6606 | 3.3423 | 3.0239 | 2.7056 | 2.3873 | 2.3873 | 1.9099
|  | H2: Mimimum Circumference 6' from the Butt | Circumference at the Butt | [11 empty] | Radius at the Butt in Inches
20 | 4 | #N/A | #N/A | 31 | 29 | 27 | 25 | 23 | 21 | 19.5 | 17.5 | 14 | #N/A | #N/A | 32.7143 | 30.7143 | 28.7143 | 26.7143 | 24.7143 | 22.7143 | 21.4286 | 18.5714 | 14.8571 | 240 | #N/A | #N/A | 5.2066 | 4.8883 | 4.57 | 4.2517 | 3.9334 | 3.6151 | 3.4105 | 2.9557 | 2.3646
25 | 5 | #N/A | #N/A | 33.5 | 31.5 | 29.5 | 27.5 | 25.5 | 23 | 21.5 | 19.5 | 15 | #N/A | #N/A | 35.5526 | 33.5526 | 31.5526 | 29.5526 | 27.5526 | 24.8947 | 23.5526 | 20.9211 | 15.9474 | 300 | #N/A | #N/A | 5.6584 | 5.3401 | 5.0218 | 4.7034 | 4.3851 | 3.9621 | 3.7485 | 3.3297 | 2.5381
30 | 5.5 | #N/A | #N/A | 36.5 | 34 | 32 | 29.5 | 27.5 | 25 | 23.5 | 20.5 | #N/A | #N/A | #N/A | 38.875 | 36.25 | 34.25 | 31.625 | 29.625 | 27 | 25.625 | 21.875 | #N/A | 360 | #N/A | #N/A | 6.1871 | 5.7694 | 5.4511 | 5.0333 | 4.715 | 4.2972 | 4.0783 | 3.4815 | #N/A
35 | 6 | #N/A | #N/A | 39 | 36.5 | 34 | 31.5 | 29 | 27 | 25 | #N/A | #N/A | #N/A | #N/A | 41.4828 | 38.8793 | 36.2759 | 33.6724 | 31.069 | 29.069 | 27.069 | #N/A | #N/A | 420 | #N/A | #N/A | 6.6022 | 6.1878 | 5.7735 | 5.3591 | 4.9448 | 4.6265 | 4.3082 | #N/A | #N/A
40 | 6 | #N/A | #N/A | 41 | 38.5 | 36 | 33.5 | 31 | 28.5 | #N/A | #N/A | #N/A | #N/A | #N/A | 43.4706 | 40.8824 | 38.2941 | 35.7059 | 33.1176 | 30.5294 | #N/A | #N/A | #N/A | 480 | #N/A | #N/A | 6.9186 | 6.5066 | 6.0947 | 5.6828 | 5.2708 | 4.8589 | #N/A | #N/A | #N/A
45 | 6.5 | #N/A | #N/A | 43 | 40.5 | 37.5 | 35 | 32.5 | 30 | #N/A | #N/A | #N/A | #N/A | #N/A | 45.4615 | 42.8846 | 39.7308 | 37.1538 | 34.5769 | 32 | #N/A | #N/A | #N/A | 540 | #N/A | #N/A | 7.2354 | 6.8253 | 6.3233 | 5.9132 | 5.5031 | 5.093 | #N/A | #N/A | #N/A
50 | 7 | 50.5 | 47.5 | 45 | 42 | 39 | 36.5 | 34 | #N/A | #N/A | #N/A | #N/A | 53.1591 | 50.0227 | 47.4545 | 44.3182 | 41.1818 | 38.6136 | 36.0455 | #N/A | #N/A | #N/A | #N/A | 600 | 8.4605 | 7.9614 | 7.5526 | 7.0535 | 6.5543 | 6.1456 | 5.7368 | #N/A | #N/A | #N/A | #N/A
55 | 7.5 | 52 | 49.5 | 46.5 | 43.5 | 40.5 | 38 | #N/A | #N/A | #N/A | #N/A | #N/A | 54.5714 | 52.0102 | 48.8878 | 45.7653 | 42.6429 | 40.0816 | #N/A | #N/A | #N/A | #N/A | #N/A | 660 | 8.6853 | 8.2777 | 7.7807 | 7.2838 | 6.7868 | 6.3792 | #N/A | #N/A | #N/A | #N/A | #N/A
60 | 8 | 54 | 51 | 48 | 45 | 42 | 39 | #N/A | #N/A | #N/A | #N/A | #N/A | 56.5556 | 53.4444 | 50.3333 | 47.2222 | 44.1111 | 41 | #N/A | #N/A | #N/A | #N/A | #N/A | 720 | 9.0011 | 8.5059 | 8.0108 | 7.5157 | 7.0205 | 6.5254 | #N/A | #N/A | #N/A | #N/A | #N/A
65 | 8.5 | 55.5 | 52.5 | 49.5 | 46.5 | 43.5 | 40.5 | #N/A | #N/A | #N/A | #N/A | #N/A | 57.9915 | 54.8898 | 51.7881 | 48.6864 | 45.5847 | 42.4831 | #N/A | #N/A | #N/A | #N/A | #N/A | 780 | 9.2296 | 8.736 | 8.2423 | 7.7487 | 7.255 | 6.7614 | #N/A | #N/A | #N/A | #N/A | #N/A
70 | 9 | 57 | 54 | 51 | 48 | 45 | 41.5 | #N/A | #N/A | #N/A | #N/A | #N/A | 59.4375 | 56.3438 | 53.25 | 50.1562 | 47.0625 | 43.4219 | #N/A | #N/A | #N/A | #N/A | #N/A | 840 | 9.4598 | 8.9674 | 8.475 | 7.9826 | 7.4902 | 6.9108 | #N/A | #N/A | #N/A | #N/A | #N/A
75 | 9.5 | 59 | 55.5 | 52.5 | 49 | 46 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 61.4348 | 57.8043 | 54.7174 | 51.087 | 48 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 900 | 9.7776 | 9.1998 | 8.7085 | 8.1307 | 7.6394 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
80 | 10 | 60 | 57 | 54 | 50.5 | 47 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 62.3514 | 59.2703 | 56.1892 | 52.5676 | 48.9459 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 960 | 9.9235 | 9.4332 | 8.9428 | 8.3664 | 7.79 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
85 | 10.5 | 61.5 | 58.5 | 55 | 51.5 | 48 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 63.8165 | 60.7405 | 57.1266 | 53.5127 | 49.8987 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1020 | 10.1567 | 9.6672 | 9.092 | 8.5168 | 7.9416 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
90 | 11 | 63 | 59.5 | 56 | 53 | 49 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 65.2857 | 61.6786 | 58.0714 | 55 | 50.8571 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1080 | 10.3905 | 9.8164 | 9.2424 | 8.7535 | 8.0942 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
95 | 11 | 64.5 | 61 | 57 | 54 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 66.7584 | 63.1573 | 59.0225 | 55.9551 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1140 | 10.6249 | 10.0518 | 9.3937 | 8.9055 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
100 | 11 | 65.5 | 62 | 58.5 | 54 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 67.7021 | 64.1064 | 60.5106 | 55.8511 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1200 | 10.7751 | 10.2028 | 9.6306 | 8.889 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
105 |  | 67 | 63 | 59.5 | 56 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 69.1818 | 65.0606 | 61.4697 | 57.8788 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | 1260 | 11.0106 | 10.3547 | 9.7832 | 9.2117 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A

## Conductor
Code Word | Size (AWG or kcmil) | Stranding (Al/Stl) | Type | Diameter (ins.) | [8 empty] | Rated Strength (lbs.) | Resistance |  | Allowable Ampacity (Amps)
|  |  |  | Individual Wires |  |  |  | Weight Per 1000 ft. (lbs.) |  |  | Content (%) |  |  | OHMS/1000 ft.
|  |  |  | Al | Stl | Core Steel | Cable Complete | Al | Stl | Total | Al | Stl |  | DC @ 20°C | AC @ 75°C |  | GMR
Turkey | 6 | 6/1 | ACSR | 0.0661 | 0.0661 | 0.0661 | 0.198 | 24 | 12 | 36 | 67.88 | 32.12 | 1190 | 0.641 | 0.806 | 105
Swan | 4 | 6/1 | ACSR | 0.0834 | 0.0834 | 0.0834 | 0.25 | 39 | 18 | 57 | 67.87 | 32.12 | 1860 | 0.403 | 0.515 | 140
Swanate | 4 | 7/1 | ACSR | 0.0772 | 0.103 | 0.103 | 0.257 | 39 | 28 | 67 | 58.1 | 41.9 | 2360 | 0.399 | 0.519 | 140
Sparrow | 2 | 6/1 | ACSR | 0.1052 | 0.1052 | 0.1052 | 0.316 | 62 | 29 | 91 | 67.9 | 32.1 | 2850 | 0.254 | 0.332 | 184
Sparate | 2 | 7/1 | ACSR | 0.0974 | 0.1298 | 0.1298 | 0.325 | 62 | 45 | 107 | 58.12 | 41.88 | 3460 | 0.251 | 0.338 | 184
Robin | 1 | 6/1 | ACSR | 0.1181 | 0.1181 | 0.1181 | 0.354 | 78 | 37 | 115 | 67.88 | 32.12 | 3550 | 0.201 | 0.268 | 212
Raven | 1/0 | 6/1 | ACSR | 0.1327 | 0.1327 | 0.1327 | 0.398 | 99 | 47 | 145 | 67.89 | 32.11 | 4380 | 0.159 | 0.217 | 242
Quail | 2/0 | 6/1 | ACSR | 0.1489 | 0.1489 | 0.1489 | 0.447 | 124 | 59 | 183 | 67.88 | 32.12 | 5310 | 0.126 | 0.176 | 276
Pigeon | 3/0 | 6/1 | ACSR | 0.1672 | 0.1672 | 0.1672 | 0.502 | 156 | 74 | 230 | 67.87 | 32.13 | 6620 | 0.1 | 0.144 | 315
Penguin | 4/0 | 6/1 | ACSR | 0.1878 | 0.1878 | 0.1878 | 0.563 | 197 | 93 | 291 | 67.89 | 32.12 | 8350 | 0.0795 | 0.119 | 357
Waxwing | 266.8 | 18/1 | ACSR | 0.1217 | 0.1217 | 0.1217 | 0.609 | 250 | 39 | 289 | 86.43 | 13.57 | 6880 | 0.0643 | 0.0787 | 449 | 0.0197
Partridge | 266.8 | 26/7 | ACSR | 0.1013 | 0.0788 | 0.2363 | 0.642 | 251 | 115 | 367 | 68.51 | 31.49 | 11300 | 0.0637 | 0.0779 | 475 | 0.0217
Ostrich | 300 | 26/7 | ACSR | 0.1074 | 0.0835 | 0.2506 | 0.68 | 283 | 130 | 412 | 68.51 | 31.49 | 12700 | 0.0567 | 0.0693 | 492
Merlin | 336.4 | 18/1 | ACSR | 0.1367 | 0.1367 | 0.1367 | 0.684 | 315 | 49 | 365 | 86.43 | 13.57 | 8680 | 0.051 | 0.0625 | 519 | 0.0221
Linnet | 336.4 | 26/7 | ACSR | 0.1137 | 0.0885 | 0.2654 | 0.72 | 317 | 146 | 462 | 68.51 | 31.49 | 14100 | 0.0505 | 0.0618 | 529 | 0.0244
Oriole | 336.4 | 30/7 | ACSR | 0.1059 | 0.1059 | 0.3177 | 0.741 | 318 | 209 | 526 | 60.35 | 39.65 | 17300 | 0.0502 | 0.0613 | 535 | 0.0255
Chickadee | 397.5 | 18/1 | ACSR | 0.1486 | 0.1486 | 0.1486 | 0.743 | 373 | 58 | 431 | 86.43 | 13.57 | 9940 | 0.0432 | 0.0529 | 576 | 0.024
Brant | 397.5 | 24/7 | ACSR | 0.1287 | 0.0858 | 0.2574 | 0.772 | 374 | 137 | 511 | 73.21 | 26.79 | 14600 | 0.043 | 0.0526 | 584
Ibis | 397.5 | 26/7 | ACSR | 0.1236 | 0.0962 | 0.2885 | 0.783 | 374 | 172 | 546 | 68.51 | 31.49 | 16300 | 0.0428 | 0.0523 | 587 | 0.0265
Lark | 397.5 | 30/7 | ACSR | 0.1151 | 0.1151 | 0.3453 | 0.806 | 375 | 247 | 622 | 60.35 | 39.65 | 20300 | 0.0425 | 0.0519 | 594 | 0.0277
Pelican | 477 | 18/1 | ACSR | 0.1628 | 0.1628 | 0.1628 | 0.814 | 447 | 70 | 517 | 86.44 | 13.56 | 11800 | 0.036 | 0.0442 | 646 | 0.0263
Flicker | 477 | 24/7 | ACSR | 0.141 | 0.094 | 0.2819 | 0.846 | 449 | 164 | 614 | 73.21 | 26.79 | 17200 | 0.0358 | 0.0439 | 655 | 0.0283
Hawk | 477 | 26/7 | ACSR | 0.1354 | 0.1053 | 0.316 | 0.858 | 449 | 207 | 656 | 68.51 | 31.49 | 19500 | 0.0356 | 0.0436 | 659 | 0.029
Hen | 477 | 30/7 | ACSR | 0.1261 | 0.1261 | 0.3783 | 0.883 | 450 | 296 | 746 | 60.35 | 39.65 | 23800 | 0.0354 | 0.0433 | 666 | 0.0304
Osprey | 556.5 | 18/1 | ACSR | 0.1758 | 0.1758 | 0.1758 | 0.879 | 522 | 82 | 603 | 86.43 | 13.57 | 13700 | 0.0308 | 0.0379 | 711 | 0.0284
Parakeet | 556.5 | 24/7 | ACSR | 0.1523 | 0.1015 | 0.3045 | 0.914 | 524 | 192 | 716 | 73.21 | 26.79 | 19800 | 0.0307 | 0.0376 | 721 | 0.0306
Dove | 556.5 | 26/7 | ACSR | 0.1463 | 0.1138 | 0.3413 | 0.927 | 524 | 241 | 765 | 68.51 | 31.49 | 22600 | 0.0306 | 0.0375 | 726 | 0.0313
Eagle | 556.5 | 30/7 | ACSR | 0.1362 | 0.1362 | 0.4086 | 0.953 | 525 | 345 | 871 | 60.35 | 39.65 | 27800 | 0.0303 | 0.0372 | 734 | 0.0328
Peacock | 605 | 24/7 | ACSR | 0.1588 | 0.1059 | 0.3177 | 0.953 | 570 | 209 | 779 | 73.2 | 26.8 | 21600 | 0.0282 | 0.0346 | 760 | 0.0319
Squab | 605 | 26/7 | ACSR | 0.1525 | 0.1186 | 0.3559 | 0.966 | 570 | 262 | 832 | 68.51 | 31.49 | 24300 | 0.0281 | 0.0345 | 765
WoodDuck | 605 | 30/7 | ACSR | 0.142 | 0.142 | 0.426 | 0.994 | 571 | 375 | 946 | 60.35 | 39.65 | 28900 | 0.0279 | 0.0342 | 774
Teal | 605 | 30/19 | ACSR | 0.142 | 0.0852 | 0.426 | 0.994 | 571 | 367 | 939 | 60.86 | 39.14 | 30000 | 0.0279 | 0.0342 | 773
Kingbird | 636 | 18/1 | ACSR | 0.188 | 0.188 | 0.188 | 0.94 | 596 | 94 | 690 | 86.43 | 13.57 | 15700 | 0.027 | 0.0332 | 773 | 0.0301
Swift | 636 | 36/1 | ACSR | 0.1329 | 0.1329 | 0.1329 | 0.93 | 596 | 47 | 643 | 92.72 | 7.28 | 13690 | 0.0271 | 0.0334 | 769 | 0.03
Rook | 636 | 24/7 | ACSR | 0.1628 | 0.1085 | 0.3256 | 0.977 | 599 | 219 | 818 | 73.22 | 26.78 | 22600 | 0.0268 | 0.033 | 784 | 0.0327
Grosbeak | 636 | 26/7 | ACSR | 0.1564 | 0.1216 | 0.3649 | 0.991 | 599 | 275 | 874 | 68.51 | 31.49 | 25200 | 0.0267 | 0.0328 | 789 | 0.0335
Scoter | 636 | 30/7 | ACSR | 0.1456 | 0.1456 | 0.4368 | 1.019 | 600 | 395 | 995 | 60.35 | 39.65 | 30400 | 0.0256 | 0.0325 | 798
Egret | 636 | 30/19 | ACSR | 0.1456 | 0.0874 | 0.4368 | 1.019 | 600 | 386 | 987 | 60.85 | 39.15 | 31500 | 0.0266 | 0.0326 | 798 | 0.0351
Flamingo | 666.6 | 24/7 | ACSR | 0.1667 | 0.1111 | 0.3333 | 1 | 628 | 230 | 858 | 73.21 | 26.79 | 23700 | 0.0256 | 0.0315 | 807 | 0.0335
Gannet | 666.6 | 26/7 | ACSR | 0.1601 | 0.1245 | 0.3736 | 1.014 | 628 | 289 | 916 | 68.51 | 31.49 | 26400 | 0.0255 | 0.0313 | 812
Stilt | 715.5 | 24/7 | ACSR | 0.1727 | 0.1151 | 0.3453 | 1.036 | 674 | 247 | 920 | 73.21 | 26.79 | 25500 | 0.0239 | 0.0294 | 844
Starling | 715.5 | 26/7 | ACSR | 0.1659 | 0.129 | 0.3871 | 1.051 | 674 | 310 | 984 | 68.51 | 31.49 | 28400 | 0.0238 | 0.0292 | 849 | 0.0355
Redwing | 715.5 | 30/19 | ACSR | 0.1544 | 0.0927 | 0.4633 | 1.081 | 676 | 435 | 1110 | 60.85 | 39.15 | 34600 | 0.0236 | 0.029 | 859 | 0.0372
Coot | 795 | 36/1 | ACSR | 0.1486 | 0.1486 | 0.1486 | 1.04 | 745 | 58 | 804 | 92.72 | 7.28 | 16710 | 0.0217 | 0.0268 | 884 | 0.0335
Drake | 795 | 26/7 | ACSR | 0.1749 | 0.136 | 0.408 | 1.107 | 749 | 344 | 1093 | 68.51 | 31.49 | 31500 | 0.0214 | 0.0263 | 907 | 0.0375
Tern | 795 | 45/7 | ACSR | 0.1329 | 0.0886 | 0.2658 | 1.063 | 749 | 146 | 895 | 83.67 | 16.33 | 22100 | 0.0216 | 0.0269 | 887 | 0.0352
Condor | 795 | 54/7 | ACSR | 0.1213 | 0.1213 | 0.364 | 1.092 | 749 | 274 | 1023 | 73.21 | 26.79 | 28200 | 0.0215 | 0.0272 | 889 | 0.0368
Mallard | 795 | 30/19 | ACSR | 0.1628 | 0.0977 | 0.4884 | 1.14 | 751 | 483 | 1234 | 60.86 | 39.14 | 38400 | 0.0213 | 0.0261 | 918 | 0.0392
Ruddy | 900 | 45/7 | ACSR | 0.1414 | 0.0943 | 0.2828 | 1.131 | 848 | 165 | 1013 | 83.67 | 16.33 | 24400 | 0.0191 | 0.0239 | 958 | 0.0374
Canary | 900 | 54/7 | ACSR | 0.1291 | 0.1291 | 0.3873 | 1.162 | 848 | 310 | 1158 | 73.22 | 26.78 | 31900 | 0.019 | 0.0241 | 961 | 0.0392
Rail | 954 | 45/7 | ACSR | 0.1456 | 0.0971 | 0.2912 | 1.165 | 899 | 175 | 1074 | 83.67 | 16.33 | 25900 | 0.018 | 0.0225 | 993 | 0.0385
Cardinal | 954 | 54/7 | ACSR | 0.1329 | 0.1329 | 0.3987 | 1.196 | 899 | 329 | 1227 | 73.21 | 26.79 | 33800 | 0.0179 | 0.0228 | 996 | 0.0404
Ortolan | 1033.5 | 45/7 | ACSR | 0.1515 | 0.101 | 0.3031 | 1.212 | 973 | 190 | 1163 | 83.67 | 16.33 | 27700 | 0.0167 | 0.0209 | 1043 | 0.0401
Curlew | 1033.5 | 54/7 | ACSR | 0.1383 | 0.1383 | 0.415 | 1.245 | 973 | 356 | 1330 | 73.21 | 26.79 | 36600 | 0.0165 | 0.0211 | 1047 | 0.042
Bluejay | 1113 | 45/7 | ACSR | 0.1573 | 0.1048 | 0.3145 | 1.258 | 1048 | 205 | 1253 | 83.67 | 16.33 | 29800 | 0.0155 | 0.0194 | 1092 | 0.0416
Finch | 1113 | 54/19 | ACSR | 0.1436 | 0.0861 | 0.4307 | 1.292 | 1053 | 375 | 1429 | 73.72 | 26.28 | 39100 | 0.0154 | 0.0197 | 1093 | 0.0436
Bunting | 1192.5 | 45/7 | ACSR | 0.1628 | 0.1085 | 0.3256 | 1.302 | 1123 | 219 | 1343 | 83.67 | 16.33 | 32000 | 0.0144 | 0.0182 | 1139 | 0.0431
Grackle | 1192.5 | 54/19 | ACSR | 0.1486 | 0.0892 | 0.4458 | 1.337 | 1129 | 402 | 1531 | 73.72 | 26.28 | 41900 | 0.0144 | 0.0184 | 1140 | 0.0451
Bittern | 1272 | 45/7 | ACSR | 0.1681 | 0.1121 | 0.3362 | 1.345 | 1198 | 234 | 1432 | 83.67 | 16.33 | 34100 | 0.0135 | 0.0171 | 1184 | 0.0445
Pheasant | 1272 | 54/19 | ACSR | 0.1535 | 0.0921 | 0.4605 | 1.381 | 1204 | 429 | 1633 | 73.71 | 26.29 | 43600 | 0.0135 | 0.0173 | 1187 | 0.0466
Dipper | 1351.5 | 45/7 | ACSR | 0.1733 | 0.1155 | 0.3466 | 1.386 | 1273 | 248 | 1521 | 83.67 | 16.33 | 36200 | 0.0127 | 0.0162 | 1229 | 0.0459
Martin | 1351.5 | 54/19 | ACSR | 0.1582 | 0.0949 | 0.4746 | 1.424 | 1279 | 456 | 1735 | 73.72 | 26.28 | 46300 | 0.0127 | 0.0163 | 1232 | 0.048
Bobolink | 1431 | 45/7 | ACSR | 0.1783 | 0.1189 | 0.3566 | 1.427 | 1348 | 263 | 1611 | 83.67 | 16.33 | 38300 | 0.012 | 0.0153 | 1272 | 0.0472
Lapwing | 1590 | 45/7 | ACSR | 0.188 | 0.1253 | 0.3759 | 1.504 | 1498 | 292 | 1790 | 83.67 | 16.33 | 42200 | 0.0108 | 0.0139 | 1354 | 0.0498
Falcon | 1590 | 54/19 | ACSR | 0.1716 | 0.103 | 0.5148 | 1.544 | 1505 | 536 | 2041 | 73.72 | 26.28 | 54500 | 0.0108 | 0.014 | 1359 | 0.0521
Chukar | 1780 | 84/19 | ACSR | 0.1456 | 0.0874 | 0.4368 | 1.602 | 1685 | 386 | 2072 | 81.35 | 18.65 | 51000 | 0.0097 | 0.0125 | 1453 | 0.0534
Mockingbird | 2034.5 | 72/7 | ACSR | 0.1681 | 0.1122 | 0.337 | 1.681 | 1929 | 234 | 2163 | 89.2 | 18.7 | 46800 | 0.0085 | 0.0112 | 1546 | 0.0553
Bluebird | 2156 | 84/19 | ACSR | 0.1602 | 0.0962 | 0.4808 | 1.762 | 2040 | 468 | 2508 | 81.34 | 18.66 | 60300 | 0.00801 | 0.0105 | 1623 | 0.0588
Kiwi | 2167 | 72/7 | ACSR | 0.1735 | 0.1157 | 0.347 | 1.735 | 2051 | 249 | 2300 | 89.17 | 10.82 | 49800 | 0.00801 | 0.0106 | 1607 | 0.057
Peachbell | 6 | 7 | AAC | A |  |  | 0.184 | 0.0206 |  | 25 |  |  | 563 | 0.658 | 0.805 | 103 | 0.00555
Rose | 4 | 7 | AAC | A |  |  | 0.232 | 0.0328 |  | 39 |  |  | 881 | 0.414 | 0.506 | 138 | 0.007
Iris | 2 | 7 | AAC | AA, A |  |  | 0.292 | 0.0522 |  | 62 |  |  | 1350 | 0.26 | 0.318 | 185 | 0.00883
Pansy | 1 | 7 | AAC | AA, A |  |  | 0.328 | 0.0657 |  | 78 |  |  | 1640 | 0.207 | 0.252 | 214 | 0.00991
Poppy | 1/0 | 7 | AAC | AA, A |  |  | 0.368 | 0.0829 |  | 99 |  |  | 1990 | 0.164 | 0.2 | 247 | 0.0111
Aster | 2/0 | 7 | AAC | AA, A |  |  | 0.414 | 0.1045 |  | 125 |  |  | 2510 | 0.13 | 0.159 | 286 | 0.0125
Phlox | 3/0 | 7 | AAC | AA, A |  |  | 0.464 | 0.1317 |  | 157 |  |  | 3040 | 0.103 | 0.126 | 331 | 0.014
Oxlip | 4/0 | 7 | AAC | AA, A |  |  | 0.522 | 0.1663 |  | 198 |  |  | 3830 | 0.0817 | 0.0999 | 383 | 0.0158
Sneezewort | 250 | 7 | AAC | AA |  |  | 0.567 | 0.1964 |  | 234 |  |  | 4520 | 0.0691 | 0.0846 | 425 | 0.0171
Valerian | 250 | 19 | AAC | A |  |  | 0.574 | 0.1963 |  | 234 |  |  | 4660 | 0.0691 | 0.0846 | 426 | 0.0181
Daisy | 266.8 | 7 | AAC | AA |  |  | 0.586 | 0.2095 |  | 250 |  |  | 4830 | 0.0648 | 0.0793 | 443 | 0.0177
Laurel | 266.8 | 19 | AAC | A |  |  | 0.592 | 0.2095 |  | 250 |  |  | 4970 | 0.0648 | 0.0793 | 444 | 0.0187
Peony | 300 | 19 | AAC | A |  |  | 0.628 | 0.2358 |  | 281 |  |  | 5480 | 0.0576 | 0.0706 | 478 | 0.0198
Tulip | 336.4 | 19 | AAC | A |  |  | 0.665 | 0.2644 |  | 315 |  |  | 6150 | 0.0514 | 0.063 | 513 | 0.021
Daffodil | 350 | 19 | AAC | A |  |  | 0.679 | 0.2748 |  | 328 |  |  | 6390 | 0.0494 | 0.0605 | 526 | 0.0214
Canna | 397.5 | 19 | AAC | AA, A |  |  | 0.723 | 0.312 |  | 373 |  |  | 7110 | 0.0435 | 0.0534 | 570 | 0.0228
Goldentuft | 450 | 19 | AAC | AA |  |  | 0.769 | 0.3534 |  | 422 |  |  | 7890 | 0.0384 | 0.0472 | 616 | 0.0243
Cosmos | 477 | 19 | AAC | AA |  |  | 0.792 | 0.3744 |  | 447 |  |  | 8360 | 0.0362 | 0.0445 | 639 | 0.025
Syringa | 477 | 37 | AAC | A |  |  | 0.795 | 0.3744 |  | 447 |  |  | 8690 | 0.0362 | 0.0445 | 639 | 0.0254
Zinnia | 500 | 19 | AAC | AA |  |  | 0.811 | 0.3926 |  | 469 |  |  | 8760 | 0.0346 | 0.0425 | 658 | 0.0256
Hyacinth | 500 | 37 | AAC | AA |  |  | 0.814 | 0.3924 |  | 469 |  |  | 9110 | 0.0346 | 0.0425 | 658
Dahlia | 556.5 | 19 | AAC | AA |  |  | 0.856 | 0.4369 |  | 522 |  |  | 9750 | 0.0311 | 0.0382 | 703 | 0.027
Mistletoe | 556.5 | 37 | AAC | AA |  |  | 0.858 | 0.4368 |  | 522 |  |  | 9940 | 0.0311 | 0.0382 | 704 | 0.0275
Meadowsweet | 600 | 37 | AAC | AA |  |  | 0.891 | 0.4709 |  | 562 |  |  | 10700 | 0.0228 | 0.0355 | 738 | 0.0285
Orchid | 636 | 37 | AAC | AA, A |  |  | 0.918 | 0.4995 |  | 596 |  |  | 11400 | 0.0272 | 0.0335 | 765 | 0.0294
Heuchera | 650 | 37 | AAC | AA |  |  | 0.928 | 0.5102 |  | 609 |  |  | 11600 | 0.0266 | 0.0328 | 775 | 0.0297
Verbena | 700 | 37 | AAC | AA |  |  | 0.963 | 0.5494 |  | 656 |  |  | 12500 | 0.0247 | 0.0305 | 812 | 0.0308
Flag | 700 | 61 | AAC | A |  |  | 0.964 | 0.5495 |  | 656 |  |  | 12900 | 0.0247 | 0.0305 | 812
Violet | 715.5 | 37 | AAC | AA |  |  | 0.973 | 0.5623 |  | 671 |  |  | 12800 | 0.0242 | 0.0299 | 823 | 0.0312
Nasturtium | 715.5 | 61 | AAC | AA |  |  | 0.975 | 0.5619 |  | 671 |  |  | 13100 | 0.0242 | 0.0299 | 823 | 0.0314
Petunia | 750 | 37 | AAC | AA |  |  | 0.997 | 0.5893 |  | 703 |  |  | 13100 | 0.023 | 0.0286 | 847 | 0.0319
Cattail | 750 | 61 | AAC | AA |  |  | 0.998 | 0.5892 |  | 703 |  |  | 13500 | 0.023 | 0.0286 | 847
Arbutus | 795 | 37 | AAC | AA |  |  | 1.026 | 0.6245 |  | 745 |  |  | 13900 | 0.0217 | 0.027 | 878 | 0.0328
Lilac | 795 | 61 | AAC | A |  |  | 1.027 | 0.6248 |  | 745 |  |  | 14300 | 0.0217 | 0.027 | 879 | 0.0331
Cockscomb | 900 | 37 | AAC | AA |  |  | 1.092 | 0.7072 |  | 844 |  |  | 15400 | 0.0192 | 0.0239 | 948 | 0.0349
Snapdragon | 900 | 61 | AAC | AA |  |  | 1.093 | 0.7072 |  | 844 |  |  | 15900 | 0.0192 | 0.0239 | 948
Magnolia | 954 | 37 | AAC | AA |  |  | 1.124 | 0.7495 |  | 894 |  |  | 16400 | 0.0181 | 0.0226 | 982 | 0.036
Goldenrod | 954 | 61 | AAC | A |  |  | 1.125 | 0.7498 |  | 894 |  |  | 16900 | 0.0181 | 0.0226 | 983 | 0.0362
Hawkweed | 1000 | 37 | AAC | AA |  |  | 1.151 | 0.7854 |  | 937 |  |  | 17200 | 0.0173 | 0.0216 | 1010 | 0.0368
Camellia | 1000 | 61 | AAC | AA |  |  | 1.152 | 0.7849 |  | 937 |  |  | 17700 | 0.0713 | 0.0216 | 1011
Bluebell | 1033.5 | 37 | AAC | AA |  |  | 1.17 | 0.8114 |  | 969 |  |  | 17700 | 0.0167 | 0.021 | 1031 | 0.0374
Larkspur | 1033.5 | 61 | AAC | AA |  |  | 1.171 | 0.8122 |  | 969 |  |  | 18300 | 0.0167 | 0.021 | 1032 | 0.0377
Marigold | 1113 | 61 | AAC | AA, A |  |  | 1.216 | 0.8744 |  | 1043 |  |  | 19700 | 0.0155 | 0.0195 | 1079 | 0.0391
Hawthorn | 1192.5 | 61 | AAC | AA, A |  |  | 1.258 | 0.9363 |  | 1118 |  |  | 21100 | 0.0145 | 0.0183 | 1124 | 0.0405
Narcissus | 1272 | 61 | AAC | AA, A |  |  | 1.3 | 0.999 |  | 1192 |  |  | 22000 | 0.0136 | 0.0173 | 1169 | 0.0418
Columbine | 1351.5 | 61 | AAC | AA, A |  |  | 1.34 | 1.0608 |  | 1267 |  |  | 23400 | 0.0128 | 0.0163 | 1212 | 0.0431
Carnation | 1431 | 61 | AAC | AA, A |  |  | 1.378 | 1.1244 |  | 1341 |  |  | 24300 | 0.0121 | 0.0155 | 1253 | 0.0444
Gladiolus | 1510.5 | 61 | AAC | A |  |  | 1.416 | 1.1869 |  | 1416 |  |  | 25600 | 0.0144 | 0.0147 | 1294
Coreopsis | 1590 | 61 | AAC | AA |  |  | 1.453 | 1.248 |  | 1490 |  |  | 27000 | 0.0109 | 0.0141 | 1333 | 0.0468
Jessamine | 1750 | 61 | AAC | AA |  |  | 1.524 | 1.3748 |  | 1640 |  |  | 29700 | 0.00988 | 0.0129 | 1408 | 0.049
Cowslip | 2000 | 91 | AAC | A |  |  | 1.631 | 1.5697 |  | 1875 |  |  | 34200 | 0.00864 | 0.0115 | 1518 | 0.0525
Sagebrush | 2250 | 91 | AAC | A |  |  | 1.73 | 1.7662 |  | 2130 |  |  | 37500 | 0.00776 | 0.0105 | 1612
Lupine | 2500 | 91 | AAC | A |  |  | 1.823 | 1.9623 |  | 2366 |  |  | 41900 | 0.00698 | 0.00969 | 1706 | 0.0588
Bitterroot | 2750 | 91 | AAC | A |  |  | 1.912 | 2.1589 |  | 2603 |  |  | 46100 | 0.00635 | 0.009 | 1793
Trillium | 3000 | 127 | AAC | A |  |  | 1.998 | 2.3564 |  | 2839 |  |  | 50300 | 0.00582 | 0.00834 | 1874 | 0.0646
Bluebonnet | 3500 | 127 | AAC | A |  |  | 2.158 | 2.7486 |  | 3345 |  |  | 58700 | 0.00499 | 0.00756 | 2024 | 0.0697
1/4" U | Utilities | 3 | OHGW |  |  |  | 0.25 |  |  | 117 |  |  | 3150
1/4" U | Utilities | 3 | OHGW |  |  |  | 0.25 |  |  | 117 |  |  | 4500
5/16" U | Utilities | 3 | OHGW |  |  |  | 0.3125 |  |  | 171 |  |  | 6500
3/8" U | Utilities | 3 | OHGW |  |  |  | 0.375 |  |  | 220 |  |  | 8500
3/16" U | Utilities | 7 | OHGW |  |  |  | 0.1875 |  |  | 80 |  |  | 2400
9/32" U | Utilities | 7 | OHGW |  |  |  | 0.2813 |  |  | 164 |  |  | 4600
5/16" U | Utilities | 7 | OHGW |  |  |  | 0.3125 |  |  | 225 |  |  | 6000
3/8" U | Utilities | 7 | OHGW |  |  |  | 0.375 |  |  | 273 |  |  | 11500
7/16" U | Utilities | 7 | OHGW |  |  |  | 0.4375 |  |  | 399 |  |  | 18000
1/2" U | Utilities | 7 | OHGW |  |  |  | 0.5 |  |  | 517 |  |  | 25000
1/4" C | Common | 3 | OHGW |  |  |  | 0.25 |  |  | 117 |  |  | 1860
5/16" C | Common | 3 | OHGW |  |  |  | 0.3125 |  |  | 171 |  |  | 2490
3/8" C | Common | 3 | OHGW |  |  |  | 0.375 |  |  | 220 |  |  | 3330
3/16" C | Common | 7 | OHGW |  |  |  | 0.1875 |  |  | 73 |  |  | 1150
7/32" C | Common | 7 | OHGW |  |  |  | 0.2188 |  |  | 98 |  |  | 1540
1/4" C | Common | 7 | OHGW |  |  |  | 0.25 |  |  | 121 |  |  | 1900
9/32" C | Common | 7 | OHGW |  |  |  | 0.2813 |  |  | 164 |  |  | 2570
5/16" C | Common | 7 | OHGW |  |  |  | 0.3125 |  |  | 205 |  |  | 3200
3/8" C | Common | 7 | OHGW |  |  |  | 0.375 |  |  | 273 |  |  | 4250
7/16" C | Common | 7 | OHGW |  |  |  | 0.4375 |  |  | 399 |  |  | 5700
1/2" C | Common | 7 | OHGW |  |  |  | 0.5 |  |  | 517 |  |  | 7400
9/16" C | Common | 7 | OHGW |  |  |  | 0.5625 |  |  | 671 |  |  | 9600
5/8" C | Common | 7 | OHGW |  |  |  | 0.625 |  |  | 813 |  |  | 11600
1/2" C | Common | 19 | OHGW |  |  |  | 0.5 |  |  | 504 |  |  | 7620
9/16" C | Common | 19 | OHGW |  |  |  | 0.5625 |  |  | 637 |  |  | 9640
5/8" C | Common | 19 | OHGW |  |  |  | 0.625 |  |  | 796 |  |  | 11000
3/4" C | Common | 19 | OHGW |  |  |  | 0.75 |  |  | 1155 |  |  | 16000
7/8" C | Common | 19 | OHGW |  |  |  | 0.875 |  |  | 1581 |  |  | 21900
1" C | Common | 19 | OHGW |  |  |  | 1 |  |  | 2073 |  |  | 28700
1/4" SM | Siemens-Martin | 3 | OHGW |  |  |  | 0.25 |  |  | 117 |  |  | 3040
5/16" SM | Siemens-Martin | 3 | OHGW |  |  |  | 0.3125 |  |  | 171 |  |  | 4090
3/8" SM | Siemens-Martin | 3 | OHGW |  |  |  | 0.375 |  |  | 220 |  |  | 5560
3/16" SM | Siemens-Martin | 7 | OHGW |  |  |  | 0.1875 |  |  | 73 |  |  | 1900
7/32" SM | Siemens-Martin | 7 | OHGW |  |  |  | 0.2188 |  |  | 98 |  |  | 2560
1/4" SM | Siemens-Martin | 7 | OHGW |  |  |  | 0.25 |  |  | 121 |  |  | 3150
9/32" SM | Siemens-Martin | 7 | OHGW |  |  |  | 0.2813 |  |  | 164 |  |  | 4250
5/16" SM | Siemens-Martin | 7 | OHGW |  |  |  | 0.3125 |  |  | 205 |  |  | 5350
3/8" SM | Siemens-Martin | 7 | OHGW |  |  |  | 0.375 |  |  | 273 |  |  | 6950
7/16" SM | Siemens-Martin | 7 | OHGW |  |  |  | 0.4375 |  |  | 399 |  |  | 9350
1/2" SM | Siemens-Martin | 7 | OHGW |  |  |  | 0.5 |  |  | 517 |  |  | 12100
9/16" SM | Siemens-Martin | 7 | OHGW |  |  |  | 0.5625 |  |  | 671 |  |  | 15700
5/8" SM | Siemens-Martin | 7 | OHGW |  |  |  | 0.625 |  |  | 813 |  |  | 19100
1/2" SM | Siemens-Martin | 19 | OHGW |  |  |  | 0.5 |  |  | 504 |  |  | 12700
9/16" SM | Siemens-Martin | 19 | OHGW |  |  |  | 0.5625 |  |  | 637 |  |  | 16100
5/8" SM | Siemens-Martin | 19 | OHGW |  |  |  | 0.625 |  |  | 796 |  |  | 18100
3/4" SM | Siemens-Martin | 19 | OHGW |  |  |  | 0.75 |  |  | 1155 |  |  | 26200
7/8" SM | Siemens-Martin | 19 | OHGW |  |  |  | 0.875 |  |  | 1581 |  |  | 35900
1" SM | Siemens-Martin | 19 | OHGW |  |  |  | 1 |  |  | 2073 |  |  | 47000
1/4" HSS | High Strength | 3 | OHGW |  |  |  | 0.25 |  |  | 117 |  |  | 4730
5/16" HSS | High Strength | 3 | OHGW |  |  |  | 0.3125 |  |  | 171 |  |  | 6350
3/8" HSS | High Strength | 3 | OHGW |  |  |  | 0.375 |  |  | 220 |  |  | 8360
3/16" HSS | High Strength | 7 | OHGW |  |  |  | 0.1875 |  |  | 73 |  |  | 2850
7/32" HSS | High Strength | 7 | OHGW |  |  |  | 0.2188 |  |  | 98 |  |  | 3850
1/4" HSS | High Strength | 7 | OHGW |  |  |  | 0.25 |  |  | 121 |  |  | 4750
9/32" HSS | High Strength | 7 | OHGW |  |  |  | 0.2813 |  |  | 164 |  |  | 6400
5/16" HSS | High Strength | 7 | OHGW |  |  |  | 0.3125 |  |  | 205 |  |  | 8000
3/8" HSS | High Strength | 7 | OHGW |  |  |  | 0.375 |  |  | 273 |  |  | 10800
7/16" HSS | High Strength | 7 | OHGW |  |  |  | 0.4375 |  |  | 399 |  |  | 14500
1/2" HSS | High Strength | 7 | OHGW |  |  |  | 0.5 |  |  | 517 |  |  | 18800
9/16" HSS | High Strength | 7 | OHGW |  |  |  | 0.5625 |  |  | 671 |  |  | 24500
5/8" HSS | High Strength | 7 | OHGW |  |  |  | 0.625 |  |  | 813 |  |  | 29600
1/2" HSS | High Strength | 19 | OHGW |  |  |  | 0.5 |  |  | 504 |  |  | 19100
9/16" HSS | High Strength | 19 | OHGW |  |  |  | 0.5625 |  |  | 637 |  |  | 24100
5/8" HSS | High Strength | 19 | OHGW |  |  |  | 0.625 |  |  | 796 |  |  | 28100
3/4" HSS | High Strength | 19 | OHGW |  |  |  | 0.75 |  |  | 1155 |  |  | 40800
7/8" HSS | High Strength | 19 | OHGW |  |  |  | 0.875 |  |  | 1581 |  |  | 55800
1" HSS | High Strength | 19 | OHGW |  |  |  | 1 |  |  | 2073 |  |  | 73200
1/4" EHSS | Extra High Strength | 3 | OHGW |  |  |  | 0.25 |  |  | 117 |  |  | 6740
5/16" EHSS | Extra High Strength | 3 | OHGW |  |  |  | 0.3125 |  |  | 171 |  |  | 9100
3/8" EHSS | Extra High Strength | 3 | OHGW |  |  |  | 0.375 |  |  | 220 |  |  | 11800
3/16" EHSS | Extra High Strength | 7 | OHGW |  |  |  | 0.1875 |  |  | 73 |  |  | 3990
7/32" EHSS | Extra High Strength | 7 | OHGW |  |  |  | 0.2188 |  |  | 98 |  |  | 5400
1/4" EHSS | Extra High Strength | 7 | OHGW |  |  |  | 0.25 |  |  | 121 |  |  | 6650
9/32" EHSS | Extra High Strength | 7 | OHGW |  |  |  | 0.2813 |  |  | 164 |  |  | 8950
5/16" EHSS | Extra High Strength | 7 | OHGW |  |  |  | 0.3125 |  |  | 205 |  |  | 11200
3/8" EHSS | Extra High Strength | 7 | OHGW |  |  |  | 0.375 |  |  | 273 |  |  | 15400
7/16" EHSS | Extra High Strength | 7 | OHGW |  |  |  | 0.4375 |  |  | 399 |  |  | 20800
1/2" EHSS | Extra High Strength | 7 | OHGW |  |  |  | 0.5 |  |  | 517 |  |  | 26900
9/16" EHSS | Extra High Strength | 7 | OHGW |  |  |  | 0.5625 |  |  | 671 |  |  | 35000
5/8" EHSS | Extra High Strength | 7 | OHGW |  |  |  | 0.625 |  |  | 813 |  |  | 42400
1/2" EHSS | Extra High Strength | 19 | OHGW |  |  |  | 0.5 |  |  | 504 |  |  | 26700
9/16" EHSS | Extra High Strength | 19 | OHGW |  |  |  | 0.5625 |  |  | 637 |  |  | 33700
5/8" EHSS | Extra High Strength | 19 | OHGW |  |  |  | 0.625 |  |  | 796 |  |  | 40200
3/4" EHSS | Extra High Strength | 19 | OHGW |  |  |  | 0.75 |  |  | 1155 |  |  | 58300
7/8" EHSS | Extra High Strength | 19 | OHGW |  |  |  | 0.875 |  |  | 1581 |  |  | 79700
1" EHSS | Extra High Strength | 19 | OHGW |  |  |  | 1 |  |  | 2073 |  |  | 104500

## Anchors
Anchor Unit | Maximum Holding Power (lbs)
GAP8 | 16000
GAP11 | 23000
GAP20 | 36000
GAS8 | 6000
GAS12 | 12000

## Pole Class
Table 1
Wood Pole Class Size (Nominal Strength)
Class | Lateral (Horizontal) Load, lbs.
Size | (applied 2 ft. from tip)
H6 | 11400
H5 | 10000
H4 | 8700
H3 | 7500
H2 | 6400
H1 | 5400
1 | 4500
2 | 3700
3 | 3000
4 | 2400
5 | 1900
6 | 1500
7 | 1200
9 | 740
10 | 370

## Ruling Span
Span Lengths |  | Ruling Span = | 163.8438
111 | 1367631
163 | 4330747
177 | 5545233
106 | 1191016
120 | 1728000
88 | 681472
212 | 9528128
182 | 6028568
170 | 4913000
182 | 6028568
170 | 4913000
175 | 5359375
187 | 6539203
176 | 5451776
91 | 753571
95 | 857375
192 | 7077888
133 | 2352637
127 | 2048383
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
^Insert Spans above this line^

## NESC 232-1
2002 NESC TABLE 232-1
Nature of surface underneath wires, conductors, or cables | Insulated communication conductors and cable; messengers; surge-protection wires, grounded guys; ungrounded guys exposed to 0 to 300 V neutral conductors meeting Rule 230E1; supply cables meeting Rule 230C1 (ft) | Noninsulated communication conductors; supply cables of 0 to 750 V meeting Rules 230C2 or 230C3 (ft) | Supply cables over 750 V meeting Rules 230C2 or 230C3; open supply conductors, 0 to 750 V ungrounded guys exposed to over 300 V to 750V14 (ft) | Open supply conductors, over 750 V 0 to 22 kV; ungrounded guys exposed to750 V to 22kV (ft) | Trolley and electrified railroad contact conductors and associated span or messenger wires
[5 empty] | 0 to 750 V to ground (ft.) | Over 750 V to 22 KV to ground (ft.)
Where wires, conductors, or cables cross over or overhang
1. Track rails of railroads(except electrifiedrailroads using overheadtrolley conductors)2’ 16 | 23.5 | 24 | 24.5 | 26.5 | 22 | 22
2. Roads, streets, and otherareas subject to trucktraffic 23 | 15.5 | 16 | 16.5 | 18.5 | 18 | 20
3.Driveways, parking lots,and alleys | 15.5 | 16 | 16.5 | 18.5 | 18 | 20
4. Other land traversed byvehicles, such ascultivated, grazmg,forest, orchards, etc.26 | 15.5 | 16 | 16.5 | 18.5 | - | -
5. Spaces and ways subjectto pedestrians or restricted traffic only9 | 9.5 | 12 | 12.5 | 14.5 | 16 | 18
6. Water areas not suitablefor sailboating or wheresailboatmg isprohibited2’ | 14 | 14.5 | 15 | 17 | - | -
7. Water areas suitable for sailbo ating including lakes, ponds, reservoirs, tidal waters, rivers, streams, and canals with an unobstructed surface area of’7’ 18, 19, 20,21
a. Lessthan2Oacres | 17.5 | 18 | 18.5 | 20.5
b. Over2Oto200acres | 25.5 | 26 | 26.5 | 28.5
c. Over200 to 2000 acres | 31.5 | 32 | 32.5 | 34.5
d. Over2000acres | 37.5 | 38 | 38.5 | 40.5
8. Established boat ramps and associated rigging areas; areas posted with sign(s) for rigging or launching boats | Clearance above ground shall be 5 ft greater than in 7 above, for the type of water areas served by the launching site
Where wires, conductors, or cables run along and within the limits of the highways or other road rights-of-way but not overhang the roadway
9. Roads, streets, or alleys | 15.5 | 16 | 16.5 | 18.5 | 18 | 20
10. Roads in rural districts where it is unlikely that vehicles will be crossing under the line | 13.5 | 14 | 14.5 | 16.5 | 18 | 20
From Table 232-1. Vertical Clearance of Wires, Conductors, and Cables Above Ground, Roadway, Rail, or Water Surfaces, published in the 2002 National Electrical Safety Code (NESC); Copyright © 2001, IEEE. All rights reserved.

## NESC 253-1
NESC 253-1
Overload Factors for Poles, Guys, Anchors, Etc.
(Use with Table 261-1A Strength Factors)
Overload Factors for Grade
|  | B | C
Rule 250B Loads | Vertical Loads | 1.5 | 1.5
Transverse Loads | Wind | 2.5 | 2.2
| Wire Tension | 1.65 | 1.3
Longitudinal Loads | In General | 1.1 | No Req't
| At Deadends | 1.65 | 1.3
| At Deadends (for guys) | 1.65 | 1.1

## NESC 261-1A
Table 2
(NESC Table 261-1A)
Strength Factors for Structures, Crossarms, Support Hardware, Guys,
Foundations, and Anchors for Use with Overload Factors of NESC Table 253-1
Grade
|  | B | C
Strength factors for use with loads of Rule 250B | Metal and Prestressed-Concrete Structures | 1 | 1
| Wood and Reinforced-Concrete Structures | 0.65 | 0.85
| Support Hardware | 1 | 1
| Guy Wire | 0.9 | 0.9
| Guy Anchor and Foundation | 1 | 1
Strength factors for use with loads of Rule 250C | Metal and Prestressed-Concrete Structures | 1 | 1
| Wood and Reinforced-Concrete Structures | 0.75 | 0.75
| Support Hardware | 1 | 1
| Guy Wire | 0.9 | 0.9
| Guy Anchor and Foundation | 1 | 1

## Union Steel Poles
Union Metal Corp Pole Data
Catalog Number | Pole Hgt | Class | Top Dia | Base Dia | Wall Thickness | Ultimate Moment Capacity at GL (ft-kips) | Galvanized Weight (lbs) | Embedment Depth (ft) | Shape
30CL1-R | 30 | 1 | 6 | 10.2 | 0.188 | 68.01 | 506 | 5 | Round
35CL1-R | 35 | 1 | 6.4 | 11.3 | 0.188 | 84.04 | 645 | 5.5 | Round
40CL1-R | 40 | 1 | 6.4 | 12 | 0.188 | 94.69 | 766 | 6 | Round
45CL1-R | 45 | 1 | 6.4 | 12.7 | 0.188 | 105.97 | 895 | 6.5 | Round
50CL1-R | 50 | 1 | 7.2 | 13.68 | 0.188 | 123.46 | 1132 | 7 | Round
55CL1-R | 55 | 1 | 7.2 | 14.38 | 0.188 | 136.3 | 1278 | 7.5 | Round
60CL1-R | 60 | 1 | 7.2 | 15.08 | 0.188 | 149.77 | 1471 | 8 | Round
65CL1-R | 65 | 1 | 7.2 | 15.78 | 0.188 | 163.87 | 1631 | 8.5 | Round
70CL1-R | 70 | 1 | 7.2 | 16.48 | 0.188 | 178.61 | 1800 | 9 | Round
75CL1-R | 75 | 1 | 7.2 | 17.18 | 0.188 | 193.99 | 1975 | 9.5 | Round
80CL1-R | 80 | 1 | 7.2 | 17.88 | 0.188 | 210 | 2159 | 10 | Round
85CL1-R | 85 | 1 | 7.2 | 18.58 | 0.188 | 226.64 | 2350 | 10.5 | Round
30CL2-R | 30 | 2 | 7.1 | 11.3 | 0.12 | 55.44 | 374 | 5 | Round
35CL2-R | 35 | 2 | 7.5 | 12.4 | 0.12 | 65.99 | 471 | 5.5 | Round
40CL2-R | 40 | 2 | 8.3 | 13.9 | 0.12 | 80.84 | 601 | 6 | Round
45CL2-R | 45 | 2 | 8.3 | 14.6 | 0.12 | 87.85 | 697 | 6.5 | Round
50CL2-R | 50 | 2 | 6 | 12.48 | 0.188 | 100.77 | 994 | 7 | Round
55CL2-R | 55 | 2 | 6 | 13.18 | 0.188 | 112.4 | 1128 | 7.5 | Round
60CL2-R | 60 | 2 | 6 | 13.88 | 0.188 | 124.66 | 1305 | 8 | Round
65CL2-R | 65 | 2 | 6 | 14.58 | 0.188 | 137.55 | 1453 | 8.5 | Round
70CL2-R | 70 | 2 | 6 | 15.28 | 0.188 | 151.08 | 1610 | 9 | Round
75CL2-R | 75 | 2 | 6 | 15.98 | 0.188 | 165.25 | 1773 | 9.5 | Round
80CL2-R | 80 | 2 | 6 | 16.68 | 0.188 | 180.05 | 1944 | 10 | Round
﻿30CL3-R | 30 | 3 | 5.9 | 10.1 | 0.12 | 43.41 | 324 | 5 | Round
35CL3-R | 35 | 3 | 6.3 | 11.2 | 0.12 | 53.65 | 413 | 5.5 | Round
40CL3-R | 40 | 3 | 6.3 | 11.9 | 0.12 | 60.44 | 491 | 6 | Round
45CL3-R | 45 | 3 | 6.7 | 13 | 0.12 | 70.61 | 598 | 6.5 | Round
50CL3-R | 50 | 3 | 7.3 | 13.92 | 0.12 | 79.54 | 740 | 7 | Round
55CL3-R | 55 | 3 | 7.3 | 14.62 | 0.12 | 86.5 | 836 | 7.5 | Round
60CL3-R | 60 | 3 | 4.8 | 12.68 | 0.188 | 101.85 | 1146 | 8 | Round
65CL3-R | 65 | 3 | 4.8 | 13.38 | 0.188 | 113.54 | 1282 | 8.5 | Round
70CL3-R | 70 | 3 | 4.8 | 14.08 | 0.188 | 125.86 | 1425 | 9 | Round
75CL3-R | 75 | 3 | 4.8 | 14.78 | 0.188 | 138.81 | 1576 | 9.5 | Round
80CL3-R | 80 | 3 | 4.8 | 15.48 | 0.188 | 152.41 | 1734 | 10 | Round
85CL3-R | 85 | 3 | 4.8 | 16.18 | 0.188 | 166.63 | 1899 | 10.5 | Round
﻿30CL4-R | 30 | 4 | 5.5 | 9.7 | 0.12 | 39.73 | 308 | 5 | Round
35CL4-R | 35 | 4 | 5.5 | 10.4 | 0.12 | 45.6 | 375 | 5.5 | Round
40CL4-R | 40 | 4 | 5.5 | 11.1 | 0.12 | 51.88 | 447 | 6 | Round
45CL4-R | 45 | 4 | 5.5 | 11.8 | 0.12 | 58.57 | 523 | 6.5 | Round
50CL4-R | 50 | 4 | 5.9 | 12.52 | 0.12 | 65.1 | 640 | 7 | Round
55CL4-R | 55 | 4 | 5.9 | 13.22 | 0.12 | 71.43 | 746 | 7.5 | Round
60CL4-R | 60 | 4 | 5.9 | 13.92 | 0.12 | 78.03 | 837 | 8 | Round
65CL4-R | 65 | 4 | 5.9 | 14.62 | 0.12 | 84.93 | 933 | 8.5 | Round
70CL4-R | 70 | 4 | 3.6 | 12.88 | 0.188 | 102.94 | 1156 | 9 | Round
75CL4-R | 75 | 4 | 3.6 | 13.58 | 0.188 | 114.68 | 1375 | 9.5 | Round
80CL4-R | 80 | 4 | 3.6 | 14.28 | 0.188 | 127.06 | 1520 | 10 | Round
85CL4-R | 85 | 4 | 3.6 | 14.98 | 0.188 | 140.08 | 1672 | 10.5 | Round
﻿30CL5-R | 30 | 5 | 4.4 | 8.6 | 0.12 | 30.44 | 262 | 5 | Round
35CL5-R | 35 | 5 | 4.4 | 9.3 | 0.12 | 35.61 | 321 | 5.5 | Round
40CL5-R | 40 | 5 | 4.4 | 10 | 0.12 | 41.18 | 386 | 6 | Round
45CL5-R | 45 | 5 | 4.4 | 10.7 | 0.12 | 47.16 | 455 | 6.5 | Round
50CL5-R | 50 | 5 | 4.5 | 11.12 | 0.12 | 50.66 | 544 | 7 | Round
55CL5-R | 55 | 5 | 4.4 | 11.72 | 0.12 | 56.19 | 630 | 7.5 | Round
60CL5-R | 60 | 5 | 4.4 | 12.42 | 0.12 | 62.77 | 710 | 8 | Round
65CL5-R | 65 | 5 | 4.4 | 13.12 | 0.12 | 68.98 | 796 | 8.5 | Round
70CL5-R | 70 | 5 | 4.4 | 13.82 | 0.12 | 75.48 | 886 | 9 | Round
75CL5-R | 75 | 5 | 4.4 | 14.52 | 0.12 | 82.27 | 981 | 9.5 | Round
80CL5-R | 80 | 5 | 3.6 | 14.28 | 0.188 | 127.06 | 1520 | 10 | Round
85CL5-R | 85 | 5 | 3.6 | 14.98 | 0.188 | 140.08 | 1672 | 10.5 | Round
30CLH1-R | 30 | H1 | 6.8 | 11 | 0.188 | 80.32 | 557 | 5 | 12 Sided
35CLH1-R | 35 | H1 | 7.2 | 12.1 | 0.188 | 97.67 | 706 | 5.5 | 12 Sided
40CLH1-R | 40 | H1 | 7.2 | 12.8 | 0.188 | 109.12 | 835 | 6 | 12 Sided
45CLH1-R | 45 | H1 | 7.6 | 13.9 | 0.188 | 129.21 | 1011 | 6.5 | 12 Sided
50CLH1-R | 50 | H1 | 8.25 | 14.73 | 0.188 | 145.21 | 1248 | 7 | 12 Sided
55CLH1-R | 55 | H1 | 8.25 | 45.43 | 0.188 | 159.1 | 1488 | 7.5 | 12 Sided
60CLH1-R | 60 | H1 | 8.4 | 16.28 | 0.188 | 177.18 | 1637 | 8 | 12 Sided
65CLH1-R | 65 | H1 | 8.4 | 16.98 | 0.188 | 192.5 | 1811 | 8.5 | 12 Sided
70CLH1-R | 70 | H1 | 8.4 | 17.67 | 0.188 | 208.45 | 1993 | 9 | 12 Sided
75CLH1-R | 75 | H1 | 8.4 | 18.38 | 0.188 | 225.03 | 2181 | 9.5 | 12 Sided
80CLH1-R | 80 | H1 | 7.6 | 18.28 | 0.188 / 0.250 | 289.98 | 2622 | 10 | 12 Sided
85CLH1-R | 85 | H1 | 7.6 | 18.98 | 0.188 / 0.250 | 312.53 | 2879 | 10.5 | 12 Sided
30CLH2-R | 30 | H2 | 7.6 | 11.8 | 0.188 | 93.65 | 610 | 5 | 12 Sided
35CLH2-R | 35 | H2 | 8 | 12.9 | 0.188 | 112.32 | 766 | 5.5 | 12 Sided
40CLH2-R | 40 | H2 | 8.4 | 14 | 0.188 | 132.69 | 938 | 6 | 12 Sided
45CLH2-R | 45 | H2 | 8.7 | 15 | 0.188 | 152.54 | 1117 | 6.5 | 12 Sided
50CLH2-R | 50 | H2 | 9.25 | 15.73 | 0.188 | 167.56 | 1367 | 7 | 12 Sided
55CLH2-R | 55 | H2 | 9.5 | 16.68 | 0.188 | 188.55 | 1566 | 7.5 | 12 Sided
60CLH2-R | 60 | H2 | 8.7 | 16.58 | 0.188 / 0.250 | 242.26 | 1858 | 8 | 12 Sided
65CLH2-R | 65 | H2 | 8.7 | 17.28 | 0.188 / 0.250 | 262.91 | 2093 | 8.5 | 12 Sided
70CLH2-R | 70 | H2 | 8.7 | 17.98 | 0.188 / 0.250 | 284.39 | 2336 | 9 | 12 Sided
75CLH2-R | 75 | H2 | 8.7 | 18.68 | 0.188 / 0.250 | 306.72 | 2590 | 9.5 | 12 Sided
﻿40CLH3-MS | 40 | H3 | 8.9 | 15.62 | 0.1875 | 171.73 | 996 | 6 | 12 Sided
45CLH3-MS | 45 | H3 | 8.9 | 16.46 | 0.1875 | 190.32 | 1158 | 6.5 | 12 Sided
50CLH3-MS | 50 | H3 | 8.9 | 17.3 | 0.1875 | 209.87 | 1329 | 7 | 12 Sided
55CLH3-MS | 55 | H3 | 8.9 | 17.6 | 0.1875 | 215.55 | 1585 | 7.5 | 12 Sided
60CLH3-MS | 60 | H3 | 8.9 | 18.44 | 0.1875 | 236.32 | 1768 | 8 | 12 Sided
65CLH3-MS | 65 | H3 | 8.9 | 19.28 | 0.1875 | 258.04 | 1960 | 8.5 | 12 Sided
70CLH3-MS | 70 | H3 | 8.9 | 20.12 | 0.1875 | 280.73 | 2160 | 9 | 12 Sided
75CLH3-MS | 75 | H3 | 8.9 | 20.96 | 0.1875 | 304.36 | 2369 | 9.5 | 12 Sided
80CLH3-MS | 80 | H3 | 8.9 | 21.8 | 0.1875 | 328.96 | 2586 | 10 | 12 Sided
85CLH3-MS | 85 | H3 | 8.9 | 22.64 | 0.1875 | 354.51 | 2812 | 10.5 | 12 Sided
90CLH3-MS | 90 | H3 | 8.9 | 23.48 | 0.1875 | 381.01 | 3046 | 11 | 12 Sided
95CLH3-MS | 95 | H3 | 8.9 | 24.32 | 0.1875 | 408.47 | 3300 | 11.5 | 12 Sided
100CLH3-MS | 100 | H3 | 8.9 | 25.16 | 0.1875 | 433.26 | 3552 | 12 | 12 Sided
105CLH3-MS | 105 | H3 | 8.9 | 25.45 | 0.1875 | 439.33 | 3940 | 12.5 | 12 Sided
110CLH3-MS | 110 | H3 | 8.9 | 26.29 | 0.1875 | 460.85 | 4203 | 13 | 12 Sided
115CLH3-MS | 115 | H3 | 8.9 | 27.13 | 0.1875 | 482.32 | 4475 | 13.5 | 12 Sided
120CLH3-MS | 120 | H3 | 8.9 | 27.97 | 0.1875 | 503.69 | 4756 | 14 | 12 Sided
125CLH3-MS | 125 | H3 | 8.9 | 28.81 | 0.1875 | 524.92 | 5045 | 14.5 | 12 Sided
130CLH3-MS | 130 | H3 | 8.9 | 29.65 | 0.1875 | 545.95 | 5343 | 15 | 12 Sided
﻿40CLH4-MS | 40 | H4 | 8.8 | 16.64 | 0.1875 | 192.75 | 1033 | 6 | 12 Sided
45CLH4-MS | 45 | H4 | 8.8 | 17.62 | 0.1875 | 215.79 | 1207 | 6.5 | 12 Sided
50CLH4-MS | 50 | H4 | 8.8 | 18.6 | 0.1875 | 240.13 | 1391 | 7 | 12 Sided
55CLH4-MS | 55 | H4 | 8.8 | 19.01 | 0.1875 | 249.02 | 1667 | 7.5 | 12 Sided
60CLH4-MS | 60 | H4 | 8.8 | 19.99 | 0.1875 | 275.12 | 1865 | 8 | 12 Sided
65CLH4-MS | 65 | H4 | 8.8 | 20.97 | 0.1875 | 302.52 | 2073 | 8.5 | 12 Sided
70CLH4-MS | 70 | H4 | 8.8 | 21.95 | 0.1875 | 331.22 | 2291 | 9 | 12 Sided
75CLH4-MS | 75 | H4 | 8.8 | 22.93 | 0.1875 | 361.22 | 2519 | 9.5 | 12 Sided
80CLH4-MS | 80 | H4 | 8.8 | 23.91 | 0.1875 | 392.52 | 2758 | 10 | 12 Sided
85CLH4-MS | 85 | H4 | 8.8 | 24.89 | 0.1875 | 424.43 | 3006 | 10.5 | 12 Sided
90CLH4-MS | 90 | H4 | 8.8 | 25.87 | 0.1875 | 449.55 | 3264 | 11 | 12 Sided
95CLH4-MS | 95 | H4 | 8.8 | 26.85 | 0.1875 | 474.64 | 3553 | 11.5 | 12 Sided
100CLH4-MS | 100 | H4 | 8.8 | 27.83 | 0.1875 | 499.6 | 3832 | 12 | 12 Sided
105CLH4-MS | 105 | H4 | 8.8 | 28.24 | 0.1875 | 508.37 | 4265 | 12.5 | 12 Sided
110CLH4-MS | 110 | H4 | 8.8 | 29.22 | 0.1875 | 533.06 | 4558 | 13 | 12 Sided
115CLH4-MS | 115 | H4 | 8.8 | 30.22 | 0.1875 | 557.47 | 4861 | 13.5 | 12 Sided
120CLH4-MS | 120 | H4 | 8.8 | 31.18 | 0.1875 | 581.52 | 5174 | 14 | 12 Sided
125CLH4-MS | 125 | H4 | 8.8 | 32.16 | 0.1875 | 605.13 | 5498 | 14.5 | 12 Sided
130CLH4-MS | 130 | H4 | 8.8 | 33.14 | 0.1875 | 628.22 | 5831 | 15 | 12 Sided
﻿40CLH5-MS | 40 | H5 | 9.45 | 15.97 | 0.25 | 238.26 | 1368 | 6 | 12 Sided
45CLH5-MS | 45 | H5 | 9.45 | 16.78 | 0.25 | 262.76 | 1589 | 6.5 | 12 Sided
50CLH5-MS | 50 | H5 | 9.45 | 17.6 | 0.25 | 288.46 | 1821 | 7 | 12 Sided
55CLH5-MS | 55 | H5 | 9.45 | 17.75 | 0.25 | 290.99 | 2163 | 7.5 | 12 Sided
60CLH5-MS | 60 | H5 | 9.45 | 18.57 | 0.25 | 318.01 | 2408 | 8 | 12 Sided
65CLH5-MS | 65 | H5 | 9.45 | 19.38 | 0.25 | 346.22 | 2664 | 8.5 | 12 Sided
70CLH5-MS | 70 | H5 | 9.45 | 20.2 | 0.25 | 375.63 | 2932 | 9 | 12 Sided
75CLH5-MS | 75 | H5 | 9.45 | 21.01 | 0.25 | 406.24 | 3211 | 9.5 | 12 Sided
80CLH5-MS | 80 | H5 | 9.45 | 21.83 | 0.25 | 438.06 | 3500 | 10 | 12 Sided
85CLH5-MS | 85 | H5 | 9.45 | 22.64 | 0.25 | 471.07 | 3801 | 10.5 | 12 Sided
90CLH5-MS | 90 | H5 | 9.45 | 23.46 | 0.25 | 505.28 | 4113 | 11 | 12 Sided
95CLH5-MS | 95 | H5 | 9.45 | 24.27 | 0.25 | 540.69 | 4451 | 11.5 | 12 Sided
100CLH5-MS | 100 | H5 | 9.45 | 25.09 | 0.25 | 577.29 | 4785 | 12 | 12 Sided
105CLH5-MS | 105 | H5 | 9.45 | 25.24 | 0.25 | 580.88 | 5292 | 12.5 | 12 Sided
110CLH5-MS | 110 | H5 | 9.45 | 26.05 | 0.25 | 618.8 | 5639 | 13 | 12 Sided
115CLH5-MS | 115 | H5 | 9.45 | 26.87 | 0.25 | 657.92 | 5998 | 13.5 | 12 Sided
120CLH5-MS | 120 | H5 | 9.45 | 27.68 | 0.25 | 698.25 | 6367 | 14 | 12 Sided
125CLH5-MS | 125 | H5 | 9.45 | 28.5 | 0.25 | 739.77 | 6748 | 14.5 | 12 Sided
130CLH5-MS | 130 | H5 | 9.45 | 29.31 | 0.25 | 782.49 | 7140 | 15 | 12 Sided
﻿40CLH6-MS | 40 | H6 | 10.25 | 17.09 | 0.25 | 274.47 | 1474 | 6 | 12 Sided
45CLH6-MS | 45 | H6 | 10.25 | 17.94 | 0.25 | 302.04 | 1710 | 6.5 | 12 Sided
50CLH6-MS | 50 | H6 | 10.25 | 18.8 | 0.25 | 330.93 | 1958 | 7 | 12 Sided
55CLH6-MS | 55 | H6 | 10.25 | 18.98 | 0.25 | 334.73 | 2325 | 7.5 | 12 Sided
60CLH6-MS | 60 | H6 | 10.25 | 19.84 | 0.25 | 365.11 | 2587 | 8 | 12 Sided
65CLH6-MS | 65 | H6 | 10.25 | 20.69 | 0.25 | 396.81 | 2861 | 8.5 | 12 Sided
70CLH6-MS | 70 | H6 | 10.25 | 21.55 | 0.25 | 429.83 | 3147 | 9 | 12 Sided
75CLH6-MS | 75 | H6 | 10.25 | 22.4 | 0.25 | 464.17 | 3444 | 9.5 | 12 Sided
80CLH6-MS | 80 | H6 | 10.25 | 23.26 | 0.25 | 499.83 | 3753 | 10 | 12 Sided
85CLH6-MS | 85 | H6 | 10.25 | 24.11 | 0.25 | 536.81 | 4073 | 10.5 | 12 Sided
90CLH6-MS | 90 | H6 | 10.25 | 24.97 | 0.25 | 575.12 | 4405 | 11 | 12 Sided
95CLH6-MS | 95 | H6 | 10.25 | 25.82 | 0.25 | 614.74 | 4778 | 11.5 | 12 Sided
100CLH6-MS | 100 | H6 | 10.25 | 26.68 | 0.25 | 655.68 | 5134 | 12 | 12 Sided
105CLH6-MS | 105 | H6 | 10.25 | 26.86 | 0.25 | 661.01 | 5663 | 12.5 | 12 Sided
110CLH6-MS | 110 | H6 | 10.25 | 27.72 | 0.25 | 703.44 | 6033 | 13 | 12 Sided
115CLH6-MS | 115 | H6 | 10.25 | 28.57 | 0.25 | 747.19 | 6415 | 13.5 | 12 Sided
120CLH6-MS | 120 | H6 | 10.25 | 29.43 | 0.25 | 792.26 | 6808 | 14 | 12 Sided
125CLH6-MS | 125 | H6 | 10.25 | 30.28 | 0.25 | 838.65 | 7213 | 14.5 | 12 Sided
130CLH6-MS | 130 | H6 | 10.25 | 31.14 | 0.25 | 886.36 | 7629 | 15 | 12 Sided

## Tapp Steel Poles
TransAmerican Power Products, Inc.
﻿Catalog Number | Pole Hgt | Class | Top Dia | Base Dia | Wall Thickness | Ultimate Mom. Cap. @Gnd. Line (ft. - kips) | Pole Weight (lbs.) | Gnd. Line Dia. (in.) | Shape
C1-050-116 | 50 | 1 | 7.9 | 13.52 | 0.1875 | 115.8 | 1175 | 12.68 | 12 Sided
C1-055-129 | 55 | 1 | 7.9 | 14.12 | 0.1875 | 128.7 | 1319 | 13.22 | 12 Sided
C1-060-142 | 60 | 1 | 7.9 | 14.72 | 0.1875 | 141.6 | 1470 | 13.76 | 12 Sided
C1-065-155 | 65 | 1 | 7.9 | 15.32 | 0.1875 | 154.5 | 1634 | 14.3 | 12 Sided
C1-070-168 | 70 | 1 | 7.9 | 15.92 | 0.1875 | 167.5 | 1797 | 14.84 | 12 Sided
C1-075-181 | 75 | 1 | 7.9 | 16.52 | 0.1875 | 180.5 | 1966 | 15.38 | 12 Sided
C1-080-194 | 80 | 1 | 7.9 | 17.12 | 0.1875 | 193.6 | 2142 | 15.92 | 12 Sided
C1-085-207 | 85 | 1 | 7.9 | 17.72 | 0.1875 | 206.7 | 2325 | 16.46 | 12 Sided
﻿C1-090-220 | 90 | 1 | 7.9 | 18.32 | 0.1875 | 219.9 | 2513 | 17 | 12 Sided
C2-040-74 | 40 | 2 | 5.65 | 11.25 | 0.1875 | 74.2 | 682 | 10.41 | Round
C2-045-85 | 45 | 2 | 5.65 | 11.95 | 0.1875 | 84.6 | 800 | 11.04 | Round
C2-050-95 | 50 | 2 | 5.65 | 12.27 | 0.1875 | 95.1 | 961 | 11.29 | Round
C2-055-106 | 55 | 2 | 5.65 | 12.97 | 0.1875 | 105.7 | 1090 | 11.92 | Round
﻿C2-060-116 | 60 | 2 | 5.65 | 13.67 | 0.1875 | 116.2 | 1225 | 12.55 | Round
C3-040-60 | 40 | 3 | 4.75 | 10.35 | 0.1875 | 60.1 | 608 | 9.51 | Round
C3-045-69 | 45 | 3 | 4.75 | 11.05 | 0.1875 | 68.6 | 717 | 10.14 | Round
C3-050-77 | 50 | 3 | 4.75 | 11.37 | 0.1875 | 77.1 | 864 | 10.39 | Round
C3-055-86 | 55 | 3 | 4.75 | 12.07 | 0.1875 | 85.7 | 984 | 11.02 | Round
﻿C3-060-94 | 60 | 3 | 4.75 | 12.77 | 0.1875 | 94.2 | 1110 | 11.65 | Round
C4-040-48 | 40 | 4 | 3.7 | 9.3 | 0.1875 | 48 | 521 | 8.46 | Round
C4-045-55 | 45 | 4 | 3.7 | 10 | 0.1875 | 54.8 | 619 | 9.09 | Round
C4-050-62 | 50 | 4 | 3.7 | 10.32 | 0.1875 | 61.6 | 752 | 9.34 | Round
C4-055-69 | 55 | 4 | 3.7 | 11.02 | 0.1875 | 68.5 | 860 | 9.97 | Round
﻿C4-060-75 | 60 | 4 | 3.7 | 11.72 | 0.1875 | 75.3 | 975 | 10.6 | Round
H1-050-139 | 50 | H1 | 8.3 | 14.67 | 0.1875 | 138.9 | 1261 | 13.73 | 12 Sided
H1-055-154 | 55 | H1 | 8.3 | 15.35 | 0.1875 | 154.2 | 1417 | 14.34 | 12 Sided
H1-060-170 | 60 | H1 | 8.3 | 16.02 | 0.1875 | 169.6 | 1581 | 14.94 | 12 Sided
H1-065-185 | 65 | H1 | 8.3 | 16.7 | 0.1875 | 185.1 | 1760 | 15.55 | 12 Sided
H1-070-201 | 70 | H1 | 8.3 | 17.37 | 0.1875 | 200.5 | 1938 | 16.16 | 12 Sided
H1-075-216 | 75 | H1 | 8.3 | 18.05 | 0.1875 | 216.1 | 2124 | 16.77 | 12 Sided
H1-080-232 | 80 | H1 | 8.3 | 18.72 | 0.1875 | 231.6 | 2315 | 17.37 | 12 Sided
H1-085-247 | 85 | H1 | 8.3 | 19.4 | 0.1875 | 247.3 | 2515 | 17.98 | 12 Sided
﻿H1-090-263 | 90 | H1 | 8.3 | 20.07 | 0.1875 | 263 | 2722 | 18.59 | 12 Sided
H2-060-201 | 60 | H2 | 8.6 | 17.52 | 0.1875 | 200.8 | 1709 | 16.28 | 12 Sided
H2-065-219 | 65 | H2 | 8.6 | 18.3 | 0.1875 | 219 | 1896 | 16.98 | 12 Sided
H2-070-237 | 70 | H2 | 8.6 | 19.07 | 0.1875 | 237.3 | 2091 | 17.68 | 12 Sided
H2-075-256 | 75 | H2 | 8.6 | 19.85 | 0.1875 | 255.6 | 2295 | 18.38 | 12 Sided
H2-080-274 | 80 | H2 | 8.6 | 20.62 | 0.1875 | 274 | 2507 | 19.07 | 12 Sided
H2-085-292 | 85 | H2 | 8.6 | 21.4 | 0.1875 | 292.4 | 2726 | 19.77 | 12 Sided
H2-090-311 | 90 | H2 | 8.6 | 22.17 | 0.1875 | 310.9 | 2955 | 20.47 | 12 Sided
H2-095-329 | 95 | H2 | 8.6 | 22.57 | 0.1875 | 329.4 | 3288 | 20.79 | 12 Sided
﻿H2-100-348 | 100 | H2 | 8.6 | 23.35 | 0.1875 | 348 | 3529 | 21.49 | 12 Sided
﻿H3-060-235 | 60 | H3 | 9.1 | 18.92 | 0.1875 | 235.2 | 1843 | 17.56 | 12 Sided
﻿H3-065-257 | 65 | H3 | 9.1 | 19.77 | 0.1875 | 256.5 | 2045 | 18.33 | 12 Sided
H3-070-278 | 70 | H3 | 9.1 | 20.62 | 0.1875 | 277.8 | 2256 | 19.09 | 12 Sided
H3-075-299 | 75 | H3 | 9.1 | 21.47 | 0.1875 | 299.2 | 2476 | 19.86 | 12 Sided
H3-080-321 | 80 | H3 | 9.1 | 22.32 | 0.1875 | 320.7 | 2706 | 20.62 | 12 Sided
H3-085-342 | 85 | H3 | 9.1 | 23.17 | 0.1875 | 342.2 | 2945 | 21.39 | 12 Sided
H3-090-364 | 90 | H3 | 9.1 | 24.02 | 0.1875 | 363.7 | 3192 | 22.15 | 12 Sided
H3-095-385 | 95 | H3 | 9.1 | 24.5 | 0.1875 | 385.4 | 3554 | 22.54 | 12 Sided
H3-100-407 | 100 | H3 | 9.1 | 25.35 | 0.1875 | 407.1 | 3815 | 23.31 | 12 Sided
H3-105-429 | 105 | H3 | 9.1 | 26.2 | 0.1875 | 428.8 | 4085 | 24.07 | 12 Sided
H3-110-451 | 110 | H3 | 9.1 | 27.05 | 0.1875 | 450.6 | 4364 | 24.84 | 12 Sided
H4-060-273 | 60 | H4 | 9.7 | 20.72 | 0.1875 | 272.7 | 2011 | 19.2 | 12 Sided
H4-065-297 | 65 | H4 | 9.7 | 21.67 | 0.1875 | 297.3 | 2232 | 20.06 | 12 Sided
H4-070-322 | 70 | H4 | 9.7 | 22.62 | 0.1875 | 322.1 | 2465 | 20.91 | 12 Sided
H4-075-347 | 75 | H4 | 9.7 | 23.57 | 0.1875 | 346.9 | 2707 | 21.77 | 12 Sided
H4-080-372 | 80 | H4 | 9.7 | 24.52 | 0.1875 | 371.7 | 2959 | 22.62 | 12 Sided
H4-085-397 | 85 | H4 | 9.7 | 25.47 | 0.1875 | 396.5 | 3221 | 23.48 | 12 Sided
H4-090-422 | 90 | H4 | 9.7 | 26.42 | 0.1875 | 421.5 | 3493 | 24.33 | 12 Sided
H4-095-447 | 95 | H4 | 9.7 | 27 | 0.1875 | 446.5 | 3904 | 24.81 | 12 Sided
H4-100-472 | 100 | H4 | 9.7 | 27.95 | 0.1875 | 471.5 | 4192 | 25.67 | 12 Sided
H4-105-497 | 105 | H4 | 9.7 | 28.9 | 0.1875 | 496.6 | 4491 | 26.52 | 12 Sided
﻿H4-110-522 | 110 | H4 | 9.7 | 29.85 | 0.1875 | 521.8 | 4799 | 27.38 | 12 Sided
H5-060-313 | 60 | H5 | 10 | 22.34 |  | 313.2 | 2139 | 20.65 | 12 Sided
H5-065-342 | 65 | H5 | 10 | 23.4 |  | 341.5 | 2378 | 21.6 | 12 Sided
H5-070-370 | 70 | H5 | 10 | 24.46 |  | 369.9 | 2630 | 22.56 | 12 Sided
H5-075-398 | 75 | H5 | 10 | 25.52 |  | 398.3 | 2891 | 23.51 | 12 Sided
H5-085-455 | 85 | H5 | 10 | 27.64 |  | 455.3 | 3449 | 25.42 | 12 Sided
H5-090-484 | 90 | H5 | 10 | 28.7 |  | 483.8 | 3745 | 26.37 | 12 Sided
H5-095-512 | 95 | H5 | 10 | 29.39 |  | 512.4 | 4229 | 26.95 | 12 Sided
H5-100-541 | 100 | H5 | 10 | 30.45 |  | 541.1 | 4543 | 27.91 | 12 Sided
H5-105-570 | 105 | H5 | 10 | 31.51 |  | 569.8 | 4869 | 28.86 | 12 Sided
H5-110-598 | 110 | H5 | 10 | 32.57 |  | 598.3 | 5523 | 29.81 | 12 Sided
H6-060-357 | 60 | H6 | 10.4 | 23.82 |  | 356.9 | 2274 | 21.98 | 12 Sided
H6-065-389 | 65 | H6 | 10.4 | 24.97 |  | 389.2 | 2531 | 23.02 | 12 Sided
H6-070-422 | 70 | H6 | 10.4 | 26.12 |  | 421.5 | 2799 | 24.05 | 12 Sided
H6-075-454 | 75 | H6 | 10.4 | 27.27 |  | 453.8 | 3079 | 25.09 | 12 Sided
H6-080-486 | 80 | H6 | 10.4 | 28.42 |  | 486.2 | 3370 | 26.12 | 12 Sided
H6-085-519 | 85 | H6 | 10.4 | 29.57 |  | 518.6 | 3675 | 27.16 | 12 Sided
H6-090-551 | 90 | H6 | 10.4 | 30.72 |  | 551.1 | 3991 | 28.19 | 12 Sided
H6-095-584 | 95 | H6 | 10.4 | 31.5 |  | 583.5 | 4703 | 28.85 | 12 Sided
H6-100-616 | 100 | H6 | 10.4 | 32.65 |  | 616.1 | 5095 | 29.89 | 12 Sided
H6-105-649 | 105 | H6 | 10.4 | 33.8 |  | 648.7 | 5502 | 30.92 | 12 Sided
﻿H6-110-681 | 110 | H6 | 10.4 | 34.95 |  | 681.3 | 5923 | 31.96 | 12 Sided

## McWane CI Poles
McWane Poles
Part Number | Pole Hgt | Class | Top Dia | Base Dia | Wall Thickness | Minimum Ground Line Capacity (ft-kips) | Standard Weight (lb) | Embed Depth (feet) | Shape | # of Sections
C130 | 30 | 1 | 6 | 11.2 | 0.28 | 67.2 | 776 | 5.5 | Round | 2
C135 | 35 | 1 | 6 | 11.6 | 0.28 | 80.4 | 939 | 6 | Round | 2
C140 | 40 | 1 | 6 | 12.6 | 0.28 | 93.6 | 1172 | 6 | Round | 3
C145 | 45 | 1 | 6 | 13.5 | 0.28 | 106.8 | 1362 | 6.5 | Round | 3
C150 | 50 | 1 | 6 | 14.5 | 0.28 | 119.9 | 1567 | 7 | Round | 3
C155 | 55 | 1 | 6 | 15 | 0.28 | 133.1 | 1857 | 7.5 | Round | 4
C160 | 60 | 1 | 6 | 15.9 | 0.28 | 146.3 | 2083 | 8 | Round | 4
C165 | 65 | 1 | 6 | 16.9 | 0.28 | 159.4 | 2373 | 8.5 | Round | 4
C170 | 70 | 1 | 6 | 17.4 | 0.28 | 172.6 | 2680 | 9 | Round | 5
C230 | 30 | 2 | 6 | 11.2 | 0.22 | 44.8 | 630 | 5.5 | Round | 2
C235 | 35 | 2 | 6 | 11.7 | 0.22 | 66.1 | 762 | 6 | Round | 2
C240 | 40 | 2 | 6 | 12.7 | 0.22 | 76.9 | 951 | 6 | Round | 3
C245 | 45 | 2 | 6 | 13.6 | 0.22 | 87.8 | 1105 | 6.5 | Round | 3
C250 | 50 | 2 | 6 | 14.6 | 0.22 | 98.6 | 1271 | 7 | Round | 3
C255 | 55 | 2 | 6 | 15.1 | 0.22 | 109.4 | 1506 | 7.5 | Round | 4
C260 | 60 | 2 | 6 | 16 | 0.22 | 120.3 | 1689 | 8 | Round | 4
C265 | 65 | 2 | 6 | 17 | 0.22 | 131.1 | 1883 | 8.5 | Round | 4
C270 | 70 | 2 | 6 | 17.5 | 0.22 | 141.9 | 2172 | 9 | Round | 5
C330 | 30 | 3 | 6 | 11.3 | 0.18 | 44.9 | 563 | 5.5 | Round | 2
C335 | 35 | 3 | 6 | 11.9 | 0.18 | 53.6 | 673 | 6 | Round | 2
C340 | 40 | 3 | 6 | 12.8 | 0.18 | 62.4 | 853 | 6 | Round | 3
C345 | 45 | 3 | 6 | 13.8 | 0.18 | 71.1 | 990 | 6.5 | Round | 3
C350 | 50 | 3 | 6 | 14.4 | 0.18 | 79.9 | 1138 | 7 | Round | 3
C355 | 55 | 3 | 6 | 15.3 | 0.18 | 88.7 | 1350 | 7.5 | Round | 4
C360 | 60 | 3 | 6 | 16.3 | 0.18 | 97.5 | 1513 | 8 | Round | 4
C365 | 65 | 3 | 6 | 17.2 | 0.18 | 106.2 | 1685 | 8.5 | Round | 4
C370 | 70 | 3 | 6 | 17.8 | 0.18 | 115 | 1941 | 9 | Round | 5
C430 | 30 | 4 | 6 | 11.3 | 0.18 | 44.9 | 563 | 5.5 | Round | 2
C435 | 35 | 4 | 6 | 11.9 | 0.18 | 53.6 | 673 | 6 | Round | 2
C440 | 40 | 4 | 6 | 12.8 | 0.18 | 62.4 | 853 | 6 | Round | 3
C445 | 45 | 4 | 6 | 13.8 | 0.18 | 71.1 | 990 | 6.5 | Round | 3
C450 | 50 | 4 | 6 | 14.4 | 0.18 | 79.9 | 1138 | 7 | Round | 3
C455 | 55 | 4 | 6 | 15.3 | 0.18 | 88.7 | 1350 | 7.5 | Round | 4
C460 | 60 | 4 | 6 | 16.3 | 0.18 | 97.5 | 1513 | 8 | Round | 4
C465 | 65 | 4 | 6 | 17.2 | 0.18 | 106.2 | 1685 | 8.5 | Round | 4
H130 | 30 | H1 | 8.7 | 13.9 | 0.22 | 80.7 | 842 | 5.5 | Round | 2
H135 | 35 | H1 | 8.7 | 14.4 | 0.22 | 96.5 | 994 | 6 | Round | 2
H140 | 40 | H1 | 8.7 | 15.3 | 0.22 | 112.3 | 1248 | 6 | Round | 3
H145 | 45 | H1 | 8.7 | 16.3 | 0.22 | 128.1 | 1436 | 6.5 | Round | 3
H150 | 50 | H1 | 8.7 | 17.2 | 0.22 | 143.9 | 1634 | 7 | Round | 3
H155 | 55 | H1 | 8.7 | 17.7 | 0.22 | 159.7 | 1925 | 7.5 | Round | 4
H160 | 60 | H1 | 8.7 | 18.7 | 0.22 | 175.5 | 2141 | 8 | Round | 4
H165 | 65 | H1 | 8.7 | 19.6 | 0.22 | 191.3 | 2368 | 8.5 | Round | 4
H230 | 30 | H2 | 8.7 | 13.9 | 0.28 | 95.7 | 1038 | 5.5 | Round | 2
H235 | 35 | H2 | 8.7 | 14.4 | 0.28 | 114.4 | 1226 | 6 | Round | 2
H240 | 40 | H2 | 8.7 | 15.3 | 0.28 | 133.4 | 1540 | 6 | Round | 3
H245 | 45 | H2 | 8.7 | 16.3 | 0.28 | 151.8 | 1771 | 6.5 | Round | 3
H250 | 50 | H2 | 8.7 | 17.2 | 0.28 | 170.6 | 2017 | 7 | Round | 3
H255 | 55 | H2 | 8.7 | 17.7 | 0.28 | 189.3 | 2376 | 7.5 | Round | 4
H260 | 60 | H2 | 8.7 | 18.7 | 0.28 | 208 | 2643 | 8 | Round | 4
H265 | 65 | H2 | 8.7 | 19.6 | 0.28 | 226.7 | 2924 | 8.5 | Round | 4
H330 | 30 | H3 | 8.7 | 13.9 | 0.31 | 112.1 | 1136 | 5.5 | Round | 2
H335 | 35 | H3 | 8.7 | 14.4 | 0.31 | 134.1 | 1341 | 6 | Round | 2
H340 | 40 | H3 | 8.7 | 15.3 | 0.31 | 156 | 1685 | 6 | Round | 3
H345 | 45 | H3 | 8.7 | 16.3 | 0.31 | 177.9 | 1938 | 6.5 | Round | 3
H350 | 50 | H3 | 8.7 | 17.2 | 0.31 | 199.9 | 2207 | 7 | Round | 3
H355 | 55 | H3 | 8.7 | 17.7 | 0.31 | 221.8 | 2600 | 7.5 | Round | 4
H360 | 60 | H3 | 8.7 | 18.7 | 0.31 | 243.7 | 2893 | 8 | Round | 4
H365 | 65 | H3 | 8.7 | 19.6 | 0.31 | 265.7 | 3200 | 8.5 | Round | 4

## Sheet1
| CODE WORD | AWG or kcmil | Aluminum/ Steel | GMR (Ft.)
841 | AKRON | 30.58 | 7 | 0.00599
847 | ALLIANCE | 246.9 | 7 | 0.017
842 | ALTON | 48.69 | 7 | 0.00756
843 | AMES | 77.47 | 7 | 0.00954
846 | AMHERST | 195.7 | 7 | 0.0152
845 | ANAHEIM | 155.4 | 7 | 0.0135
719 | ARBUTUS | 795.0 | 37 | 0.0328
695 | ASTER | 2/0 | 7 | 0.0125
628 | ATHABASKA/ACSS/TW | 1949.6 | 42/7 | 0.05
270 | ATHABASKA/TW | 1949.6 | 42/7 | 0.05
521 | AVOCET/ACSS/TW | 1113.0 | 30/7 | 0.0369
1085 | AVOCET/SD | 5 | 1113 | 0.0402
166 | AVOCET/TW | 1113.0 | 30/7 | 0.0369
844 | AZUSA | 123.3 | 7 | 0.012
83 | BITTERN | 1272.0 | 45/7 | 0.0445
359 | BITTERN/ACSS | 1272 | 45/7 | 0.0445
528 | BITTERN/ACSS/TW | 1272.0 | 35/7 | 0.0403
1092 | BITTERN/SD | 7 | 1272 | 0.0436
173 | BITTERN/TW | 1272.0 | 35/7 | 0.0403
1064 | BLACKBIRD | 5 | 556.5 | 0.0274
725 | BLUEBELL | 1033.5 | 37 | 0.0374
93 | BLUEBIRD | 2156.0 | 84/19 | 0.0588
368 | BLUEBIRD/ACSS | 2156 | 84/19 | 0.0588
537 | BLUEBIRD/ACSS/TW | 2156.0 | 64/19 | 0.0538
1107 | BLUEBIRD/SD | 8 | 2156 | 0.057
182 | BLUEBIRD/TW | 2156.0 | 64/19 | 0.0538
737 | BLUEBONNET | 3500.0 | 127 | 0.0697
78 | BLUEJAY | 1113.0 | 45/7 | 0.0416
355 | BLUEJAY/ACSS | 1113 | 45/7 | 0.0416
522 | BLUEJAY/ACSS/TW | 1113.0 | 33/7 | 0.0376
1086 | BLUEJAY/SD | 7 | 1113 | 0.041
167 | BLUEJAY/TW | 1113.0 | 33/7 | 0.0376
87 | BOBOLINK | 1431.0 | 45/7 | 0.0472
363 | BOBOLINK/ACSS | 1431 | 45/7 | 0.0472
532 | BOBOLINK/ACSS/TW | 1431.0 | 36/7 | 0.0427
1099 | BOBOLINK/SD | 7 | 1431 | 0.0461
177 | BOBOLINK/TW | 1431.0 | 36/7 | 0.0427
80 | BUNTING | 1192.5 | 45/7 | 0.0431
357 | BUNTING/ACSS | 1192.5 | 45/7 | 0.0431
525 | BUNTING/ACSS/TW | 1192.5 | 33/7 | 0.039
1089 | BUNTING/SD | 7 | 1192.5 | 0.0423
170 | BUNTING/TW | 1192.5 | 33/7 | 0.039
848 | BUTTE | 312.8 | 19 | 0.0202
850 | CAIRO | 465.4 | 19 | 0.0247
600 | CALUMET/ACSS/TW | 565.3 | 20/7 | 0.0304
242 | CALUMET/TW | 565.3 | 20/7 | 0.0288
70 | CANARY | 900.0 | 54/7 | 0.0392
350 | CANARY/ACSS | 900 | 54/7 | 0.0392
705 | CANNA | 397.5 | 19 | 0.0228
849 | CANTON | 394.5 | 19 | 0.0227
75 | CARDINAL | 954.0 | 54/7 | 0.0404
352 | CARDINAL/ACSS | 954 | 54/7 | 0.0404
517 | CARDINAL/ACSS/TW | 954.0 | 20/7 | 0.0362
1081 | CARDINAL/SD | 13 | 954 | 0.0384
162 | CARDINAL/TW | 954.0 | 20/7 | 0.0362
731 | CARNATION | 1431.0 | 61 | 0.0444
612 | CATAWBA/ACSS/TW | 1272.0 | 30/7 | 0.0394
254 | CATAWBA/TW | 1272.0 | 30/7 | 0.0394
609 | CHEYENNE/ACSS/TW | 1168.1 | 30/7 | 0.0378
251 | CHEYENNE/TW | 1168.1 | 30/7 | 0.0378
43 | CHICKADEE | 397.5 | 18/1 | 0.024
91 | CHUKAR | 1780.0 | 84/19 | 0.0534
367 | CHUKAR/ACSS | 1780 | 84/19 | 0.0534
536 | CHUKAR/ACSS/TW | 1780.0 | 37/19 | 0.0482
1105 | CHUKAR/SD | 8 | 1780 | 0.0519
181 | CHUKAR/TW | 1780.0 | 37/19 | 0.0482
1106 | COCKATOO/SD | 5 | 2156 | 0.0573
721 | COCKSCOMB | 900.0 | 37 | 0.0349
607 | COLUMBIA/ACSS/TW | 966.2 | 21/7 | 0.0364
249 | COLUMBIA/TW | 966.2 | 21/7 | 0.0364
730 | COLUMBINE | 1351.5 | 61 | 0.0431
66 | CONDOR | 795.0 | 54/7 | 0.0368
346 | CONDOR/ACSS | 795 | 54/7 | 0.0368
513 | CONDOR/ACSS/TW | 795.0 | 20/7 | 0.0331
1077 | CONDOR/SD | 13 | 795 | 0.0353
158 | CONDOR/TW | 795.0 | 20/7 | 0.0331
63 | COOT | 795.0 | 36/1 | 0.0335
732 | COREOPSIS | 1590.0 | 61 | 0.0468
71 | CORNCRAKE | 954.0 | 20/7 | 0.0378
707 | COSMOS | 477.0 | 19 | 0.025
1051 | COWBIRD/SD | 5 | 336.4 | 0.0217
734 | COWSLIP | 2000.0 | 91 | 0.0525
65 | CUCKOO | 795.0 | 24/7 | 0.0361
345 | CUCKOO/ACSS | 795 | 24/7 | 0.0361
629 | CUMBERLAND/ACSS/TW | 1926.9 | 42/19 | 0.0523
271 | CUMBERLAND/TW | 1926.9 | 42/19 | 0.0523
77 | CURLEW | 1033.5 | 54/7 | 0.042
354 | CURLEW/ACSS | 1033.5 | 54/7 | 0.042
520 | CURLEW/ACSS/TW | 1033.5 | 21/7 | 0.0377
1084 | CURLEW/SD | 13 | 1033.5 | 0.04
165 | CURLEW/TW | 1033.5 | 21/7 | 0.0377
704 | DAFFODIL | 350.0 | 19 | 0.0214
710 | DAHLIA | 556.5 | 19 | 0.027
700 | DAISY | 266.8 | 7 | 0.0177
851 | DARIEN | 559.5 | 19 | 0.0271
85 | DIPPER | 1351.5 | 45/7 | 0.0459
361 | DIPPER/ACSS | 1351.5 | 45/7 | 0.0459
530 | DIPPER/ACSS/TW | 1351.5 | 35/7 | 0.0415
1095 | DIPPER/SD | 7 | 1351.5 | 0.0449
175 | DIPPER/TW | 1351.5 | 35/7 | 0.0415
52 | DOVE | 556.5 | 26/7 | 0.0313
335 | DOVE/ACSS | 556.5 | 26/7 | 0.0313
508 | DOVE/ACSS/TW | 556.5 | 20/7 | 0.0286
1068 | DOVE/SD | 16 | 556.5 | 0.0311
153 | DOVE/TW | 556.5 | 20/7 | 0.0286
67 | DRAKE | 795.0 | 26/7 | 0.0375
347 | DRAKE/ACSS | 795 | 26/7 | 0.0375
514 | DRAKE/ACSS/TW | 795.0 | 20/7 | 0.0339
1078 | DRAKE/SD | 16 | 795 | 0.0364
159 | DRAKE/TW | 795.0 | 20/7 | 0.0339
53 | EAGLE | 556.5 | 30/7 | 0.0328
336 | EAGLE/ACSS | 556.5 | 30/7 | 0.0328
59 | EGRET | 636.0 | 30/19 | 0.0351
340 | EGRET/ACSS | 636 | 30/19 | 0.0351
1048 | EIDER/SD | 7 | 266.8 | 0.0199
852 | ELGIN | 652.4 | 19 | 0.0292
1055 | ERNE/SD | 5 | 397.5 | 0.0233
90 | FALCON | 1590.0 | 54/19 | 0.0521
366 | FALCON/ACSS | 1590 | 54/19 | 0.0521
535 | FALCON/ACSS/TW | 1590.0 | 42/19 | 0.0476
1103 | FALCON/SD | 13 | 1590 | 0.0512
180 | FALCON/TW | 1590.0 | 42/19 | 0.0476
79 | FINCH | 1113.0 | 54/19 | 0.0436
356 | FINCH/ACSS | 1113 | 54/19 | 0.0436
523 | FINCH/ACSS/TW | 1113.0 | 38/19 | 0.0399
1087 | FINCH/SD | 13 | 1113 | 0.0414
168 | FINCH/TW | 1113.0 | 38/19 | 0.0399
60 | FLAMINGO | 666.6 | 24/7 | 0.0335
341 | FLAMINGO/ACSS | 666.6 | 24/7 | 0.0335
47 | FLICKER | 477.0 | 24/7 | 0.0283
331 | FLICKER/ACSS | 477 | 24/7 | 0.0283
505 | FLICKER/ACSS/TW | 477.0 | 18/7 | 0.0257
1062 | FLICKER/SD | 13 | 477 | 0.0283
150 | FLICKER/TW | 477.0 | 18/7 | 0.0257
853 | FLINT | 740.8 | 37 | 0.0317
606 | FRASER/ACSS/TW | 946.7 | 35/7 | 0.0358
248 | FRASER/TW | 946.7 | 35/7 | 0.0358
1096 | FRIGATE/SD | 10 | 1351.5 | 0.0463
610 | GENESSEE/ACSS/TW | 1158.0 | 33/7 | 0.0384
252 | GENESSEE/TW | 1158.0 | 33/7 | 0.0384
723 | GOLDENROD | 954.0 | 61 | 0.0362
706 | GOLDENTUFT | 450.0 | 19 | 0.0243
1071 | GOLDFINCH/SD | 10 | 636 | 0.0311
81 | GRACKLE | 1192.5 | 54/19 | 0.0451
358 | GRACKLE/ACSS | 1192.5 | 54/19 | 0.0451
526 | GRACKLE/ACSS/TW | 1192.5 | 38/19 | 0.0412
1090 | GRACKLE/SD | 13 | 1192.5 | 0.0428
171 | GRACKLE/TW | 1192.5 | 38/19 | 0.0412
854 | GREELEY | 927.2 | 37 | 0.0354
58 | GROSBEAK | 636.0 | 26/7 | 0.0335
339 | GROSBEAK/ACSS | 636 | 26/7 | 0.0335
510 | GROSBEAK/ACSS/TW | 636.0 | 20/7 | 0.0305
1073 | GROSBEAK/SD | 16 | 636 | 0.0329
155 | GROSBEAK/TW | 636.0 | 20/7 | 0.0305
48 | HAWK | 477.0 | 26/7 | 0.029
332 | HAWK/ACSS | 477 | 26/7 | 0.029
506 | HAWK/ACSS/TW | 477.0 | 18/7 | 0.0264
1063 | HAWK/SD | 16 | 477 | 0.0291
151 | HAWK/TW | 477.0 | 18/7 | 0.0264
724 | HAWKWEED | 1000.0 | 37 | 0.0368
728 | HAWTHORN | 1192.5 | 61 | 0.0405
49 | HEN | 477.0 | 30/7 | 0.0304
333 | HEN/ACSS | 477 | 30/7 | 0.304
714 | HEUCHERA | 650.0 | 37 | 0.0297
611 | HUDSON/ACSS/TW | 1158.4 | 25/7 | 0.04
253 | HUDSON/TW | 1158.4 | 25/7 | 0.04
1052 | HUMMINGBIRD/SD | 7 | 336.4 | 0.0218
44 | IBIS | 397.5 | 26/7 | 0.0265
329 | IBIS/ACSS | 397.5 | 26/7 | 0.0265
1058 | IBIS/SD | 16 | 397.5 | 0.0261
692 | IRIS | 2 | 7 | 0.00883
1060 | JACKDAW/SD | 7 | 477 | 0.0261
627 | JAMES/ACSS/TW | 1730.6 | 39/19 | 0.0494
269 | JAMES/TW | 1730.6 | 39/19 | 0.0494
733 | JESSAMINE | 1750.0 | 61 | 0.049
96 | JOREA | 2515.0 | 76/19 | 0.0621
1059 | KESTREL/SD | 5 | 477 | 0.0257
604 | KETTLE/ACSS/TW | 957.2 | 32/7 | 0.035
247 | KETTLE/TW | 957.2 | 32/7 | 0.035
1070 | KILLDEER/SD | 7 | 636 | 0.0302
56 | KINGBIRD | 636.0 | 18/1 | 0.0301
94 | KIWI | 2167.0 | 72/7 | 0.057
369 | KIWI/ACSS | 2167 | 72/7 | 0.057
1108 | KIWI/SD | 4 | 2167 | 0.057
89 | LAPWING | 1590.0 | 45/7 | 0.0498
365 | LAPWING/ACSS | 1590 | 45/7 | 0.0498
534 | LAPWING/ACSS/TW | 1590.0 | 36/7 | 0.0449
1102 | LAPWING/SD | 7 | 1590 | 0.0484
179 | LAPWING/TW | 1590.0 | 36/7 | 0.0449
45 | LARK | 397.5 | 30/7 | 0.0277
330 | LARK/ACSS | 397.5 | 30/7 | 0.0277
726 | LARKSPUR | 1033.5 | 61 | 0.0377
701 | LAUREL | 266.8 | 19 | 0.0187
720 | LILAC | 795.0 | 61 | 0.0331
41 | LINNET | 336.4 | 26/7 | 0.0244
327 | LINNET/ACSS | 336.4 | 26/7 | 0.0244
1054 | LINNET/SD | 16 | 336.4 | 0.0245
1056 | LONGSPUR/SD | 7 | 397.5 | 0.0238
735 | LUPINE | 2500.0 | 91 | 0.0588
1074 | MACAW/SD | 5 | 795 | 0.0326
616 | MACKENZIE/ACSS/TW | 1359.7 | 36/7 | 0.042
258 | MACKENZIE/TW | 1359.7 | 36/7 | 0.042
722 | MAGNOLIA | 954.0 | 37 | 0.036
68 | MALLARD | 795.0 | 30/19 | 0.0392
348 | MALLARD/ACSS | 795 | 30/19 | 0.0392
727 | MARIGOLD | 1113.0 | 61 | 0.0391
86 | MARTIN | 1351.5 | 54/19 | 0.048
362 | MARTIN/ACSS | 1431 | 54/19 | 0.048
531 | MARTIN/ACSS/TW | 1351.5 | 39/19 | 0.0438
1097 | MARTIN/SD | 13 | 1351.5 | 0.0477
176 | MARTIN/TW | 1351.5 | 39/19 | 0.0438
605 | MAUMEE/ACSS/TW | 768.2 | 20/7 | 0.0325
245 | MAUMEE/TW | 768.2 | 20/7 | 0.0325
712 | MEADOWSWEET | 600.0 | 37 | 0.0285
40 | MERLIN | 336.4 | 18/1 | 0.0221
620 | MERRIMACK/ACSS/TW | 1433.6 | 39/19 | 0.045
262 | MERRIMACK/TW | 1433.6 | 39/19 | 0.045
619 | MIRAMICHI/ACSS/TW | 1455.3 | 36/7 | 0.0431
261 | MIRAMICHI/TW | 1455.3 | 36/7 | 0.0431
711 | MISTLETOE | 556.5 | 37 | 0.0275
92 | MOCKINGBIRD | 2034.5 | 72/7 | 0.0553
599 | MOHAWK/ACSS/TW | 571.7 | 18/7 | 0.0281
241 | MOHAWK/TW | 571.7 | 18/7 | 0.0281
601 | MYSTIC/ACSS/TW | 666.6 | 20/7 | 0.031
243 | MYSTIC/TW | 666.6 | 20/7 | 0.0304
729 | NARCISSUS | 1272.0 | 61 | 0.0418
717 | NASTURTIUM | 715.5 | 61 | 0.0314
613 | NELSON/ACSS/TW | 1257.1 | 35/7 | 0.04
255 | NELSON/TW | 1257.1 | 35/7 | 0.04
713 | ORCHID | 636.0 | 37 | 0.0294
42 | ORIOLE | 336.4 | 30/7 | 0.0255
328 | ORIOLE/ACSS | 336.4 | 30/7 | 0.0255
76 | ORTOLAN | 1033.5 | 45/7 | 0.0401
353 | ORTOLAN/ACSS | 1033.5 | 45/7 | 0.0401
519 | ORTOLAN/ACSS/TW | 1033.5 | 32/7 | 0.0363
1083 | ORTOLAN/SD | 7 | 1033.5 | 0.0378
164 | ORTOLAN/TW | 1033.5 | 32/7 | 0.0363
50 | OSPREY | 556.5 | 18/1 | 0.0284
602 | OSWEGO/ACSS/TW | 664.8 | 20/7 | 0.0325
244 | OSWEGO/TW | 664.8 | 20/7 | 0.031
524 | OXBIRD/ACSS/TW | 1192.5 | 30/7 | 0.0382
1088 | OXBIRD/SD | 5 | 1192.5 | 0.0415
169 | OXBIRD/TW | 1192.5 | 30/7 | 0.0382
697 | OXLIP | 4/0 | 7 | 0.0158
693 | PANSY | 1 | 7 | 0.00991
51 | PARAKEET | 556.5 | 24/7 | 0.0306
334 | PARAKEET/ACSS | 556.5 | 24/7 | 0.0306
507 | PARAKEET/ACSS/TW | 556.5 | 18/7 | 0.0277
1067 | PARAKEET/SD | 13 | 556.5 | 0.0302
152 | PARAKEET/TW | 556.5 | 18/7 | 0.0277
39 | PARTRIDGE | 266.8 | 26/7 | 0.0217
326 | PARTRIDGE/ACSS | 266.8 | 26/7 | 0.0217
1050 | PARTRIDGE/SD | 16 | 266.8 | 0.022
690 | PEACHBELL | 6 | 7 | 0.00555
54 | PEACOCK | 605.0 | 24/7 | 0.0319
337 | PEACOCK/ACSS | 605 | 24/7 | 0.0319
625 | PECOS/ACSS/TW | 1622.0 | 39/19 | 0.0481
267 | PECOS/TW | 1622.0 | 39/19 | 0.0481
626 | PEE DEE/ACSS/TW | 1758.6 | 37/7 | 0.0473
268 | PEE DEE/TW | 1758.6 | 37/7 | 0.0473
46 | PELICAN | 477.0 | 18/1. | 0.0263
702 | PEONY | 300.0 | 19 | 0.0198
718 | PETUNIA | 750.0 | 37 | 0.0319
84 | PHEASANT | 1272.0 | 54/19 | 0.0466
360 | PHEASANT/ACSS | 1272 | 54/19 | 0.0466
529 | PHEASANT/ACSS/TW | 1272.0 | 39/19 | 0.0426
1093 | PHEASANT/SD | 13 | 1272 | 0.0464
174 | PHEASANT/TW | 1272.0 | 39/19 | 0.0426
696 | PHLOX | 3/0 | 7 | 0.014
515 | PHOENIX/ACSS/TW | 954.0 | 30/7 | 0.0343
1079 | PHOENIX/SD | 5 | 954 | 0.0357
160 | PHOENIX/TW | 954.0 | 30/7 | 0.0343
1069 | PIPPIT/SD | 5 | 636 | 0.0291
621 | PLATTE/ACSS/TW | 1569.0 | 33/7 | 0.0439
263 | PLATTE/TW | 1569.0 | 33/7 | 0.0439
88 | PLOVER | 1431.0 | 54/19 | 0.0495
364 | PLOVER/ACSS | 1590 | 54/19 | 0.0495
533 | PLOVER/ACSS/TW | 1431.0 | 39/19 | 0.0451
1100 | PLOVER/SD | 13 | 1431 | 0.0488
178 | PLOVER/TW | 1431.0 | 39/19 | 0.0451
1098 | POPINJAY/SD | 5 | 1431 | 0.0452
694 | POPPY | 1/0 | 7 | 0.0111
622 | POTOMAC/ACSS/TW | 1557.4 | 36/7 | 0.0445
264 | POTOMAC/TW | 1557.4 | 36/7 | 0.0445
630 | POWDER/ACSS/TW | 2153.8 | 64/19 | 0.0538
272 | POWDER/TW | 2153.8 | 64/19 | 0.0538
512 | PUFFIN/ACSS/TW | 795.0 | 18/7 | 0.0323
1076 | PUFFIN/SD | 10 | 795 | 0.0343
157 | PUFFIN/TW | 795.0 | 18/7 | 0.0323
74 | RAIL | 954.0 | 45/7 | 0.0385
351 | RAIL/ACSS | 954 | 45/7 | 0.0385
516 | RAIL/ACSS/TW | 954.0 | 32/7 | 0.0349
1080 | RAIL/SD | 7 | 954 | 0.0364
161 | RAIL/TW | 954.0 | 32/7 | 0.0349
1101 | RATITE/SD | 5 | 1590 | 0.0477
72 | REDBIRD | 954.0 | 24/7 | 0.0396
62 | REDWING | 715.5 | 30/19 | 0.0372
343 | REDWING/ACSS | 715.5 | 30/19 | 0.0372
1094 | RINGDOVE/SD | 5 | 1351.5 | 0.044
623 | RIO GRANDE/ACSS/TW | 1533.3 | 39/19 | 0.0466
265 | RIO GRANDE/TW | 1533.3 | 39/19 | 0.0466
57 | ROOK | 636.0 | 24/7 | 0.0327
338 | ROOK/ACSS | 636 | 24/7 | 0.0327
509 | ROOK/ACSS/TW | 636.0 | 18/7 | 0.0296
1072 | ROOK/SD | 13 | 636 | 0.032
154 | ROOK/TW | 636.0 | 18/7 | 0.0296
691 | ROSE | 4 | 7 | 0.007
69 | RUDDY | 900.0 | 45/7 | 0.0374
349 | RUDDY/ACSS | 900 | 45/7 | 0.0374
631 | SANTEE/ACSS/TW | 2627.3 | 64/19 | 0.0594
273 | SANTEE/TW | 2627.3 | 64/19 | 0.0594
1066 | SAPSUCKER/SD | 10 | 556.5 | 0.0293
624 | SCHUYLKILL/ACSS/TW | 1657.4 | 36/7 | 0.0459
266 | SCHUYLKILL/TW | 1657.4 | 36/7 | 0.0459
527 | SCISSORTAIL/ACSS/TW | 1272.0 | 30/7 | 0.0394
1091 | SCISSORTAIL/SD | 5 | 1272 | 0.0427
172 | SCISSORTAIL/TW | 1272.0 | 30/7 | 0.0394
82 | SKYLARK | 1272.0 | 36/1 | 0.0427
1104 | SMEW/SD | 5 | 1780 | 0.0502
698 | SNEEZEWORT | 250.0 | 7 | 0.0171
518 | SNOWBIRD/ACSS/TW | 1033.5 | 30/7 | 0.0356
1082 | SNOWBIRD/SD | 5 | 1033.5 | 0.0389
163 | SNOWBIRD/TW | 1033.5 | 30/7 | 0.0356
1049 | SPOONBILL/SD | 10 | 268.8 | 0.0203
618 | ST. CROIX/ACSS/TW | 1467.8 | 33/7 | 0.0424
260 | ST. CROIX/TW | 1467.8 | 33/7 | 0.0424
61 | STARLING | 715.5 | 26/7 | 0.0355
342 | STARLING/ACSS | 715.5 | 26/7 | 0.0355
1057 | STORK/SD | 10 | 397.5 | 0.0249
1065 | SUNBIRD/SD | 7 | 556.5 | 0.0285
608 | SUWANNEE/ACSS/TW | 959.6 | 22/7 | 0.0373
250 | SUWANNEE/TW | 959.6 | 22/7 | 0.0373
55 | SWIFT | 636.0 | 36/1 | 0.03
708 | SYRINGA | 477.0 | 37 | 0.0254
64 | TERN | 795.0 | 45/7 | 0.0352
344 | TERN/ACSS | 795 | 45/7 | 0.0352
511 | TERN/ACSS/TW | 795.0 | 17/7 | 0.0312
1075 | TERN/SD | 7 | 795 | 0.0333
156 | TERN/TW | 795.0 | 17/7 | 0.0312
617 | THAMES/ACSS/TW | 1334.6 | 39/19 | 0.0436
259 | THAMES/TW | 1334.6 | 39/19 | 0.0436
95 | THRASHER | 2312.0 | 76/19 | 0.06
370 | THRASHER/ACSS | 2312 | 76/19 | 0.06
1047 | TITMOUSE/SD | 5 | 266.8 | 0.0195
1061 | TOUCAN/SD | 10 | 477 | 0.0274
73 | TOWHEE | 954.0 | 48/7 | 0.0391
736 | TRILLIUM | 3000.0 | 127 | 0.0646
615 | TRUCKEE/ACSS/TW | 1372.5 | 30/7 | 0.0409
257 | TRUCKEE/TW | 1372.5 | 30/7 | 0.0409
703 | TULIP | 336.4 | 19 | 0.021
699 | VALERIAN | 250.0 | 19 | 0.0181
715 | VERBENA | 700.0 | 37 | 0.0308
716 | VIOLET | 715.5 | 37 | 0.0312
603 | WABASH/ACSS/TW | 762.8 | 20/7 | 0.033
246 | WABASH/TW | 762.8 | 20/7 | 0.033
38 | WAXWING | 266.8 | 18/1 | 0.0197
1053 | WOODCOCK/SD | 10 | 336.4 | 0.023
614 | YUKON/ACSS/TW | 1233.6 | 38/19 | 0.042
256 | YUKON/TW | 1233.6 | 38/19 | 0.042
709 | ZINNIA | 500.0 | 19 | 0.0256