## Design Data
Substation Design Data
BUS DESIGN
Bus Size (IPS) | 1 | 1-1/2 | 2 | 2-1/2 | 3 | 3-1/2 | 4 | 5 | 6
Outside Diameter | 1.315 | 1.9 | 2.375 | 2.875 | 3.5 | 4 | 4.5 | 5.563 | 6.625
Copper, Sch 40, 48" Spacing, 24kA
1 Span, 1 Fixed | 9.101 | 14.6048 | 18.8895 | 24.7925 | 32.2024 | 38.5581 | 43.0996 | 52.3245 | 51.8182
2 Spans, Middle Fixed | 7.4629 | 11.9759 | 15.4894 | 20.3298 | 26.406 | 31.6177 | 35.3416 | 42.9061 | 42.491
3+ Spans, 1 Fixed | 8.0089 | 12.8522 | 16.6227 | 21.8174 | 28.3381 | 33.9312 | 37.9276 | 46.0456 | 45.6001
Aluminum, 6063-T6 Alloy, Sch 40, 48" Spacing, 24kA
1 Span, 1 Fixed | 9.2734 | 14.4773 | 18.9034 | 25.9207 | 32.808 | 38.4502 | 44.2249 | 56.7156 | 69.6716
2 Spans, Middle Fixed | 7.6042 | 11.8714 | 15.5008 | 21.255 | 26.9026 | 31.5292 | 36.2644 | 46.5068 | 57.1307
3+ Spans, 1 Fixed | 8.1606 | 12.74 | 16.635 | 22.8102 | 28.871 | 33.8362 | 38.9179 | 49.9097 | 61.311
Ampacity @ 40°C rise over 30°C, 2fps wind
Cu | 850 | 1270 | 1570 | 1990 | 2540 | 3020 | 3365
Al, 6063-T6 Alloy | 681 | 984 | 1234 | 1663 | 2040 | 2347 | 2664 | 3348 | 4064
Note: Spans should be applied only to specified conditions.
Ampacities | 1 | 2 | 3 | Note:
1/4"x4" Al Bar | 980 | 1760 | 2462 | Current ratings based on 30°C temperature rise over 40°C ambient horizontally mounted conductors with a 2ft/sec crosswind.
1/4"x5" Al Bar | 1184 | 2092 | 2905
3-1/4"x3-1/4"x1/4" Al Angle | 1902
4"x4"x1/4" Al Angle | 2236
4"x4" IWCB | 3360
4"x6" IWCB | 4470
8"x8" IWCB | 7550
1 - 500 MCM CU | 810 | 1296
1 - 750 MCM CU | 1040 | 1664
1 -1000 MCM CU | 1240 | 1984
NEMA Clearances for Outdoor Substations
Nom. Voltage (kV) | 15 | 25 | 34.5 | 46 | 69 | 115 | 161
BIL (kV) | 110 | 150 | 200 | 250 | 350 | 550 | 750
Cond Spacing
Ph-Ph (Cl to Cl) | 2'0" | 2'6" | 3'0" | 4'0" | 5'0" | 7'0" | 9'0"
Ph-Ground | 10" | 12" | 15" | 1'6" | 2'5" | 3'7.5" | 4'10"
Clearance above Grade | 9' | 10' | 10' | 10' | 11' | 12' | 14'
Switch Spacing (Cl to Cl)
Horngap | 3'0" | 4'0" | 5'0" | 6'0" | 7'0" | 10'0" | 14'0"
Vert. Break Disc. | 2'0" | 2'6" | 3'0" | 4'0" | 5'0" | 7'0" | 9'0"
Hor. Break Disc. | 2'6" | 3'0" | 4'0" | 5'0" | 6'0" | 9'0" | 13'0"
Min. Phase Spacing
Metal to Metal | 12" | 15" | 18" | 21" | 31" | 53" | 72"
Strain Insulators 10" Dia.
Number per String | 2 | 3 | 4 | 4 | 5 | 8 | 12
Station Post Insulators
BIL KV | TR No | Upright Cantilever (lbs) | Underhung Cantilever (Lbs) | Top BC (in) | Bottom BC (in) | Height (in) | Leakage (in)
95 | 202 | 2000 | 2000 | 3 | 3 | 7.5 | 10.5
95 | 222 | 4000 | 4000 | 5 | 5 | 7.5 | 10.5
110 | 205 | 2000 | 2000 | 3 | 3 | 10 | 15.5
110 | 225 | 4000 | 4000 | 5 | 5 | 12 | 15.5
150 | 208 | 2000 | 2000 | 3 | 3 | 14 | 24
150 | 227 | 4000 | 4000 | 5 | 5 | 15 | 24
200 | 210 | 2000 | 2000 | 3 | 3 | 18 | 37
200 | 231 | 4000 | 4000 | 5 | 5 | 20 | 37
250 | 214 | 2000 | 2000 | 3 | 3 | 22 | 43
250 | 267 | 4000 | 4000 | 5 | 5 | 24 | 43
350 | 216 | 1500 | 1500 | 3 | 3 | 30 | 72
350 | 278 | 3000 | 3000 | 5 | 5 | 30 | 72
550 | 286 | 1700 | 1700 | 5 | 5 | 45 | 99
550 | 287 | 2600 | 2600 | 5 | 5 | 45 | 99
650 | 288 | 1400 | 1400 | 5 | 5 | 54 | 116
650 | 289 | 2200 | 2200 | 5 | 5 | 54 | 116
750 | 291 | 1200 | 1200 | 5 | 5 | 62 | 132
750 | 295 | 1850 | 1850 | 5 | 5 | 62 | 132
900 | 304 | 950 | 950 | 5 | 5 | 80 | 165
900 | 308 | 1450 | 1450 | 5 | 5 | 80 | 165

## Bus Design
NESC Loading Zone |  |  | Heavy | (Heavy, Medium or Light) |  |  | Wind, psf: |  | 4 | Radial Ice (In.): |  | 0.5
Bus Material |  |  | 6061-T6 | (6063-T6, 6061-T6,Cu) |  |  | Mod of Elast E: |  | 10000000 | Max Fiber Stress Fb: |  | 28000
Pipe Schedule |  |  | 40
Max Short Circuit |  |  | 24000
Ø-Ø Spacing (In.) |  |  | 48
Support Type |  |  | 2 | (1-5) | Kse: | 0.82 | Kde: | 9.34
Size | OD | Sect Mod S | SS Red Factor Ksc | Wgt of Bus Wc | Mom of Inertia I | Short Circuit Fsc | Ice Loading Wi | Wind Loading Fw | Vibration Dampening Weight Dw | Total Bus Loading Ft | Min Cant StrengthWs | Max Bus Span Lm | Bus Defl Ld | 1/150 | y | (RUS) Ld | (RUS) 1/200 | (RUS) y | 1 Span | 2 Spans | 3+ Spans | 6063-T6 |  |  | 12KV 48" Ø-Ø | [5 empty] | 161KV 108" Ø-Ø
1 | 1.315 | 0.1328 | 0.67 | 0.581 | 0.0873 | 30.0696 | 1.1253 | 0.76858 | 0 | 30.8853 | 1806.0945 | 8.9974 | 23.4267 | 1.8741 | 0.11963 | 14.8604 | 0.89163 | 0.89025 | 9.2734 | 8.9974 | 8.1606 | 9.2734 | 7.6042 | 8.1606 | 10.1963 | 8.361 | 8.9727 | 0.92292 | -0.63641 | 0.81217 | 15.0098 | 12.3081 | 13.2087 | 8.9589 | -0.038441
1.5 | 1.9 | 0.3262 | 0.67 | 0.94 | 0.3099 | 30.0696 | 1.488 | 0.9628 | 0 | 31.1272 | 2361.6687 | 14.0464 | 30.4413 | 2.4353 | 0.28486 | 20.1544 | 1.2093 | 1.2074 | 14.4773 | 14.0464 | 12.74 | 14.4773 | 11.8714 | 12.74 | 16.2594 | 13.3327 | 14.3083 | 1.7821 | -0.71367 | 1.5683 | 23.7612 | 19.4842 | 20.9098 | 13.9864 | -0.060013
2 | 2.375 | 0.5606 | 0.67 | 1.264 | 0.6657 | 30.0696 | 1.7825 | 1.1205 | 0.367 | 31.3763 | 2774.8081 | 18.3408 | 35.5858 | 2.8469 | 0.48366 | 24.1104 | 1.4466 | 1.4444 | 18.9034 | 18.3408 | 16.635 | 18.9034 | 15.5008 | 16.635 | 21.5657 | 17.6838 | 18.9778 | 2.6622 | -0.65696 | 2.3428 | 31.2205 | 25.6008 | 27.4741 | 18.2624 | -0.07836
2.5 | 2.875 | 1.064 | 0.67 | 2.004 | 1.53 | 30.0696 | 2.0925 | 1.2865 | 0.367 | 31.6722 | 3157.1288 | 25.1492 | 40.2745 | 3.222 | 1.0004 | 28.8274 | 1.7296 | 1.727 | 25.9207 | 25.1492 | 22.8102 | 25.9207 | 21.255 | 22.8102 | 29.0335 | 23.8074 | 25.5495 | 3.1128 | -1.3418 | 2.7392 | 41.5444 | 34.0664 | 36.5591 | 25.0418 | -0.10745
3 | 3.5 | 1.724 | 0.67 | 2.621 | 3.017 | 30.0696 | 2.48 | 1.494 | 0.367 | 32.0337 | 3644.1394 | 31.8315 | 46.1815 | 3.6945 | 1.6213 | 33.601 | 2.0161 | 2.013 | 32.808 | 31.8315 | 28.871 | 32.808 | 26.9026 | 28.871 | 37.1724 | 30.4813 | 32.7117 | 4.3644 | -1.3502 | 3.8406 | 52.4505 | 43.0094 | 46.1564 | 31.6955 | -0.136
3.5 | 4 | 2.394 | 0.67 | 3.151 | 4.788 | 30.0696 | 2.79 | 1.66 | 0.546 | 32.3859 | 4018.5762 | 37.3058 | 50.6603 | 4.0528 | 2.2447 | 37.2515 | 2.2351 | 2.2317 | 38.4502 | 37.3058 | 33.8362 | 38.4502 | 31.5292 | 33.8362 | 43.8626 | 35.9673 | 38.5991 | 5.4124 | -1.3385 | 4.7629 | 61.0217 | 50.0378 | 53.6991 | 37.1464 | -0.15939
4 | 4.5 | 3.214 | 0.67 | 3.733 | 7.232 | 30.0696 | 3.1 | 1.826 | 1.093 | 32.8656 | 4380.2942 | 42.9086 | 54.9329 | 4.3946 | 2.9914 | 40.7938 | 2.4476 | 2.4439 | 44.2249 | 42.9086 | 38.9179 | 44.2249 | 36.2644 | 38.9179 | 50.6952 | 41.57 | 44.6118 | 6.4703 | -1.3386 | 5.6938 | 69.1832 | 56.7303 | 60.8813 | 42.7253 | -0.18333
5 | 5.563 | 5.451 | 0.67 | 5.057 | 15.16 | 30.0696 | 3.7591 | 2.1789 | 1.611 | 33.8923 | 5122.5261 | 55.0276 | 63.5381 | 5.0831 | 4.9802 | 47.9572 | 2.8774 | 2.873 | 56.7156 | 55.0276 | 49.9097 | 56.7156 | 46.5068 | 49.9097 | 65.5365 | 53.7399 | 57.6721 | 8.8209 | -1.2876 | 7.7624 | 86.2471 | 70.7226 | 75.8974 | 54.7925 | -0.2351
6 | 6.625 | 8.498 | 0.67 | 6.564 | 28.15 | 30.0696 | 4.4175 | 2.5315 | 1.79 | 35.0135 | 5835.0049 | 67.598 | 71.5927 | 5.7274 | 7.6079 | 54.7836 | 3.287 | 3.282 | 69.6716 | 67.598 | 61.311 | 69.6716 | 57.1307 | 61.311 | 82.0136 | 67.2512 | 72.172 | 12.342 | -0.34678 | 10.861 | 103.9776 | 85.2616 | 91.5003 | 67.3092 | -0.28881
8 | 8.625 | 16.813 | 0.67 | 9.878 | 72.51 | 30.0696 | 5.6575 | 3.1955 | 1.79 | 37.5065 | 7122.0358 | 91.8675 | 85.6397 | 6.8512 | 14.2535 | 66.8964 | 4.0138 | 4.0076 | 94.6856 | 91.8675 | 83.3234 | 94.6856 | 77.6422 | 83.3234 | 110.5385 | 90.6416 | 97.2739 | 15.8529 | -1.2259 | 13.9505 | 132.5757 | 108.7121 | 116.6666 | 91.475 | -0.3925
3x3 | 3 | 0.54 | 0.67 | 1.68 | 1.18 | 34.7328 | 3.4 | 1.328 | 0 | 36.4169 | 3531.2784 | 16.7085 | 39.1703 | 3.1336 | 0.31339 | 24.6066 | 1.4764 | 1.4741 | 17.2211 | 16.7085 | 15.1546 | 17.2211 | 14.1213 | 15.1546 | 17.2211 | 14.1213 | 15.1546 | 0 | -2.5872 | 0 | 24.8299 | 20.3605 | 21.8503 | 16.6372 | -0.071387
Note: For all equations, see RUS Bulletin 1724E-300 Design Guide for Rural Substations , Chapter 4 Section 4.11 - Rigid Bus Design.

## Physical Data
|  | Schedule 40 |  |  |  | Schedule 80 |  |  | Aluminum Single Angle (L) Conductors | [6 empty] | Recommended ACSR Size to Prevcent Vibration
Nominal Bus Size (in) | OD | Unit Weight (lb/ft) | Section Modulus (in3) | Moment of Inertia (in4) |  | Unit Weight (lb/ft) | Section Modulus (in3) | Moment of Inertia (in4) | Angle Size (in.) | Thickness (in.) | Section Area (in.2) | Weight (Ibs./ft) | Moment of Inertia (in.4) | Section Modulus (in.3) | Radius of Gyration (in.) | Nominal Bus Size in | Maximum Safe Span Length | Recommended Min. Size of ACSR MCM | Weight Per Foot lbs
1 | 1.315 | 0.581 | 0.1328 | 0.0873 |  | 0.751 | 0.1606 | 0.1056 | 2 1/2 x 2 1/2 | 1/4 | 1.19 | 1.40 | 0.69 | 0.39 | 0.76 | 1 | 5 |  | 0
1.5 | 1.9 | 0.94 | 0.3262 | 0.3099 |  | 1.256 | 0.4118 | 0.3912 | 2 1/2 x 2 1/2 | 3/8 | 1.74 | 2.05 | 0.98 | 0.56 | 0.75 | 1.5 | 7 |  | 0
2 | 2.375 | 1.264 | 0.5606 | 0.6657 |  | 1.737 | 0.7309 | 0.8679 | 3x3 | 1/4 | 1.43 | 1.68 | 1.18 | 0.54 | 0.91 | 2 | 9 | 266.8 | 0.367
2.5 | 2.875 | 2.004 | 1.064 | 1.53 |  | 2.65 | 1.339 | 1.924 | 3x3 | 3/8 | 2.10 | 2.47 | 1.70 | 0.80 | 0.90 | 2.5 | 10.75 | 266.8 | 0.367
3 | 3.5 | 2.621 | 1.724 | 3.017 |  | 3.547 | 2.225 | 3.894 | 3x3 | 1/2 | 2.74 | 3.23 | 2.16 | 1.04 | 0.89 | 3 | 13.25 | 266.8 | 0.367
3.5 | 4 | 3.151 | 2.394 | 4.788 |  | 4.326 | 3.14 | 6.281 | 4x4 | 1/4 | 1.94 | 2.28 | 2.94 | 1.00 | 1.23 | 3.5 | 15.25 | 397.5 | 0.546
4 | 4.5 | 3.733 | 3.214 | 7.232 |  | 5.183 | 4.272 | 9.611 | 4x4 | 3/8 | 2.86 | 3.38 | 4.26 | 1.48 | 1.22 | 4 | 17 | 795 | 1.093
5 | 5.563 | 5.057 | 5.451 | 15.16 |  | 7.188 | 7.432 | 20.67 | 4x4 | 1/2 | 3.75 | 4.41 | 5.46 | 1.93 | 1.21 | 5 | 21.25 | 1431 | 1.611
6 | 6.625 | 6.564 | 8.498 | 28.15 |  | 9.884 | 12.227 | 40.501 | 4x4 | 5/8 | 4.61 | 5.42 | 6.56 | 2.36 | 1.19 | 6 | 25.25 | 1590 | 1.79
8 | 8.625 | 9.878 | 16.813 | 72.51 |  | 15.008 | 24.52 | 105.743 | [7 empty] | 8 |  | 1590 | 1.79
|  | Schedule 40 |  |  |  | Schedule 80
Nominal Bus Size (in) | OD | Unit Weight (lb/ft) | Section Modulus (in3) | Moment of Inertia (in4) |  | Unit Weight (lb/ft) | Section Modulus (in3) | Moment of Inertia (in4)
1 | 1.315 | 1.83 | 0.1283 | 0.08434 |  | 2.5 | 0.1622 | 0.1066
1.5 | 1.9 | 3.19 | 0.3347 | 0.318 |  | 4.18 | 0.416 | 0.3952
2 | 2.375 | 4.21 | 0.5679 | 0.6744 |  | 5.78 | 0.7381 | 0.8765
2.5 | 2.875 | 6.12 | 0.9991 | 1.436 |  | 8.82 | 1.352 | 1.944
3 | 3.5 | 8.72 | 1.743 | 3.051 |  | 11.79 | 2.247 | 3.932
3.5 | 4 | 11.38 | 2.6 | 5.2 |  | 14.34 | 3.162 | 6.325
4 | 4.5 | 12.9 | 3.361 | 7.563 |  | 17.22 | 4.31 | 9.698
4.5 | 5 | 14.42 | 4.22 | 10.55 |  | 21.05 | 5.866 | 14.62
5 | 5.563 | 16.12 | 5.305 | 14.76 |  | 23.62 | 7.431 | 20.67
Support Type |  | KSE | KDE |  |  | Material | Max Fiber Stress Fb
Fixed Both Ends | 1 | 1 | 4.5 |  |  | Cu | 20000
Fixed One End-Simply Supported | 2 | 0.82 | 9.34 |  |  | 6061-T6 | 28000
Simply Supported Both Ends (single span) | 3 | 0.82 | 22.5 |  |  | 6063-T6 | 20000
Simply Support (two equal spans) | 4 | 0.82 | 9.34
Simply Supported (three or more equal spans) | 5 | 0.88 | 11.9
BIL kV | TR NO. | UPRIGHT CANTILEVER STRENGTH (LBS) | UNDERHUNG CANTILEVER STRENGTH (LBS) | BOLT CIRCLE |  | HEIGHT IN. | LEAKAGE DISTANCE IN.
|  |  |  | TOP IN. | BOTTOM IN.
95 | 202 | 2000 | 2000 | 3 | 3 | 7.5 | 10.5
95 | 202 | 4000 | 4000 | 5 | 5 | 7.5 | 10.5
110 | 205 | 2000 | 2000 | 3 | 3 | 10 | 15.5
110 | 225 | 4000 | 4000 | 5 | 5 | 12 | 15.5
150 | 208 | 2000 | 2000 | 3 | 3 | 14 | 24
150 | 227 | 4000 | 4000 | 5 | 5 | 15 | 24
200 | 210 | 2000 | 2000 | 3 | 3 | 18 | 37
200 | 231 | 4000 | 4000 | 5 | 5 | 20 | 37
250 | 214 | 2000 | 2000 | 3 | 3 | 22 | 43
250 | 267 | 4000 | 4000 | 5 | 5 | 24 | 43
350 | 216 | 1500 | 1500 | 3 | 3 | 30 | 72
350 | 278 | 3000 | 3000 | 5 | 5 | 30 | 72
550 | 286 | 1700 | 1700 | 5 | 5 | 45 | 99
550 | 287 | 2600 | 2600 | 5 | 5 | 45 | 99
650 | 288 | 1400 | 1400 | 5 | 5 | 54 | 116
650 | 289 | 2200 | 2200 | 5 | 5 | 54 | 116
750 | 291 | 1200 | 1200 | 5 | 5 | 62 | 132
750 | 295 | 1850 | 1850 | 5 | 5 | 62 | 132
900 | 304 | 950 | 950 | 5 | 5 | 80 | 165
900 | 308 | 1450 | 1450 | 5 | 5 | 80 | 165
1050 | 312 | 800 | 800 | 5 | 5 | 92 | 198
1050 | 316 | 1250 | 1250 | 5 | 5 | 92 | 198
1050 | 362 | 2300 | 2300 | 7 | 7 | 92 | 198
1300 | 324 | 1000 | 1000 | 5 | 5 | 106 | 231
1300 | 367 | 1450 | 1450 | 5 | 7 | 106 | 231
1300 | 368 | 2000 | 2000 | 7 | 7 | 106 | 231
1300 | 369 | 2050 | 2050 | 5 | 7 | 106 | 231
Nominal Size | Outside Diameter (Inches) | lnside Diameter (Inches) | CURRENT RATINGS IN AMPERES*
|  |  | 30° C Rise | 40° C Rise | 50° C Rise
STANDARD PIPE SIZES
1 | 1.315 | 1.062 | 850 | 975 | 1080
1.5 | 1.9 | 1.6 | 1270 | 1445 | 1600
2 | 2.375 | 2.062 | 1570 | 1780 | 1980
2.5 | 2.875 | 2.5 | 1990 | 2275 | 2525
3 | 3.5 | 3.062 | 2540 | 2870 | 3225
3.5% | 4 | 3.5 | 3020 | 3465 | 3860
4 | 4.5 | 4 | 3365 | 3810 | 4305
EXTRA HEAVY PIPE SIZES
1 | 1.315 | 0.951 | 1000 | 1140 | 1255
1899-12-31 12:00 | 1.9 | 1.494 | 1445 | 1650 | 1830
2 | 2.375 | 1.933 | 1830 | 2080 | 2325
2.5 | 2.875 | 2.315 | 2365 | 2720 | 3020
3 | 3.5 | 2.892 | 2970 | 3365 | 3710
3.5 | 4 | 3.358 | 3380 | 3860 | 4255
4 | 4.5 | 3.818 | 3840 | 4350 | 4850
* 40°C Ambient, 98% Conductivity, 60Hz, 2fps horizontal wind

## Electrical Data
Physical & Electrical Properties of Aluminum
[6 empty] | 6063-T6 |  |  |  | 6061-T6
Nominal Size in | A | B | Area sq in | Weight Ibs/ft | Inductive reactance 1 ft spacing 60 Hz microhm/ ft | DC Resistance at 20°C microhms/ ft | 60 Hz Rac/RDC at 70°C | AC Resistance at 70°C 60 Hz microhms/ft | Current Ratings Amp at 60 Hz (1) (2) (3) (4) Outdoor | DC Resistance at 20°C microhms/ft | 60 Hz Rac/RDC at 70°C | AC Resistance at 70°C 60 Hz microhms/ft | Current Ratings Amp at 60 Hz (1) (2) (3) (4) Outdoor
| Outside Diameter of Tube in | Wall Thickness in
Schedule 40 Pipe
1 | 1.315 | 0.133 | 0.494 | 0.581 | 68.24 | 31.120 | 1.00039 | 36.580 | 681 | 38.360 | 1.00032 | 43.820 | 622
1 1/2 | 1.900 | 0.145 | 0.800 | 0.940 | 59.45 | 19.220 | 1.00064 | 22.600 | 984 | 23.690 | 1.00046 | 27.070 | 900
2 | 2.375 | 0.154 | 1.075 | 1.264 | 54.15 | 14.300 | 1.00082 | 16.820 | 1234 | 17.630 | 1.00055 | 20.140 | 1128
2 1/2 | 2.875 | 0.203 | 1.704 | 2.004 | 49.85 | 9.019 | 1.00220 | 10.620 | 1663 | 11.170 | 1.00150 | 12.710 | 1520
3 | 3.500 | 0.216 | 2.228 | 2.621 | 45.19 | 6.897 | 1.00300 | 8.126 | 2040 | 8.500 | 1.00180 | 9.725 | 1865
3.5 | 4.000 | 0.226 | 2.680 | 3.151 | 42.05 | 5.736 | 1.00380 | 6.761 | 2347 | 7.070 | 1.00220 | 8.091 | 2145
4 | 4.500 | 0.237 | 3.174 | 3.733 | 39.28 | 4.842 | 1.00470 | 5.712 | 2664 | 5.968 | 1.00270 | 6.834 | 2436
5 | 5.563 | 0.258 | 4.300 | 5.057 | 34.31 | 3.574 | 1.00680 | 4.224 | 3348 | 4.406 | 1.00400 | 5.051 | 3063
6 | 6.625 | 0.280 | 3.381 | 6.364 | 30.23 | 2.754 | 1.00950 | 3.263 | 4064 | 3.394 | 1.00540 | 3.897 | 3719
Schedule 80 Pipe
1 | 1.315 | 0.179 | 0.639 | 0.751 | 68.81 | 24.060 | 1.00100 | 28.300 | 774 | 29.650 | 1.00075 | 33.840 | 707
1 1/2 | 1.900 | 0.200 | 1.068 | 1.256 | 39.89 | 14.390 | 1.00200 | 16.940 | 1137 | 17.730 | 1.00150 | 20.280 | 1039
2 | 2.375 | 0.218 | 1.477 | 1.737 | 34.56 | 10.400 | 1.00280 | 12.260 | 1446 | 12.820 | 1.00210 | 14.670 | 1322
2 1/2 | 2.875 | 0.276 | 2.254 | 2.650 | 50.23 | 6.820 | 1.00720 | 8.071 | 1907 | 8.406 | 1.00390 | 9.647 | 1746
3 | 3.500 | 0.300 | 3.016 | 3.547 | 45.55 | 5.096 | 1.01030 | 6.050 | 2363 | 6.281 | 1.00490 | 7.225 | 2199
3.5 | 4.000 | 0.318 | 3.678 | 4.326 | 42.39 | 4.178 | 1.01380 | 4.972 | 2735 | 5.150 | 1.00750 | 5.935 | 2507
4 | 4.300 | 0.337 | 4.407 | 3.183 | 39.61 | 3.487 | 1.01710 | 4.168 | 3118 | 4.298 | 1.00950 | 4.965 | 2862
5 | 5.563 | 0.375 | 6.112 | 7.188 | 34.63 | 2.515 | 1.02600 | 3.032 | 3949 | 3.099 | 1.01650 | 3.604 | 3631
6 | 6.625 | 0.432 | 8.405 | 9.884 | 30.58 | 1.829 | 1.04570 | 2.247 | 4891 | 2.254 | 1.02120 | 2.656 | 4532
Notes:
| 1 | Current ratings listed in the Tables are based on 30°C temperature rise over 40°C ambient horizontally mounted conductors, with spacing sufficient to eliminate proximity effects, generally assumed not to be significant if spacing is 18 in. or over. Conduction of heat by supporting structures and taps can appreciably affect the ratings.
| 2 | Conductors with a 2ft/sec crosswind. Nominal oxidized surface (e=0.50)
| 3 | Current Ratings for direct current are close to those of alternating current for all except the larger sizes; and for them, the increase for dc bus is about 1.5 percent.
| 4 | NEMA Standard SG1-3.02 (7/13/60) lists current rating for tubes of 57%-61 % IACS conductivity, but without stated emissivity factors. However, even after adjustment for the 53% IACS conductivity of 6063-T6 alloy (and 43% for 6061-T6 alloy), the ratings differ somewhat from those of this table.
Physical & Electrical Properties of Integral-Web Channel
Bus Conductors - 6101-T6 Alloy 55.0% IACS Conductivity (minimum)
Size |  | Wall Thickness | Area sq in | Weight Ib/ft | Moment of Inertia, in4 |  | DC Resistance Rdc-20°C microhms per ft | Current Rating DC 70°C e=0.35 Indoors | Inductive Reactance Xa-60Hz 1 ft spacing microhms per ft | Rac/ RDC70°C 60HZ | AC 60 Hz Resistance Rac-70°C microhms per ft | Current Rating AC-60HZ
A in | B in | T in |  |  | Ix-x | Iy-y
[12 empty] | Indoor e=0.35 | Outdoor e= 0.50
4 | 4 | 0.156 | 2.439 | 2.87 | 3.876 | 6.213 | 6.88 | 2260 | 39.02 | 1.020 | 7.017 | 2240 | 2520
4 | 4 | 0.250 | 3.781 | 4.45 | 5.788 | 9.213 | 4.42 | 2810 | 39,76 | 1.035 | 4.579 | 2276 | 3115
4 | 4 | 0.312 | 4.460 | 5.25 | 6.892 | 10.94 | 3.75 | 3050 | 40.80 | 1.050 | 3.940 | 2980 | 3360
6 | 4 | 0.250 | 4.780 | 5.62 | 16.35 | 12.74 | 3.50 | 3480 | 34.80 | 1.050 | 3.670 | 3400 | 3780
6 | 4 | 0.375 | 6.020 | 7.10 | 14.50 | 14.00 | 2.78 | 3900 | 36.60 | 1.080 | 3.000 | 3760 | 4180
6 | 4 | 0.375 | 6.950 | 8.17 | 22.91 | 17.45 | 2.41 | 4200 | .... | 1.090 | 2.630 | 4020 | 4470
6 | 5 | 0.375 | 7.600 | 8.94 | 25.19 | 29.78 | 2.20 | 4500 | 32.50 | 1.110 | 2.440 | 4320 | 4800
6 | 6 | 0.375 | 8.600 | 10.15 | 29.73 | 45.98 | 1.95 | 5020 | 27.60 | 1.110 | 2.160 | 4760 | 5270
6 | 6 | 0.550 | 11.22 | 13.19 | 40.05 | 60.86 | 1.49 | 5730 | 31.40 | 1.220 | 1.820 | 5190 | 5740
7 | 7 | 0.500 | 12.84 | 15.10 | 64.83 | 95.67 | 1.30 | 6530 | 27.60 | 1.210 | 1.570 | 5940 | 6540
8 | 5 | 0.375 | 9.080 | 10.68 | 52.88 | 37.59 | 1.84 | 5350 | 29.10 | 1.120 | 2.064 | 5060 | 5560
8 | 5 | 0.500 | 11.75 | 13.82 | 66.84 | 46.67 | 1.42 | 6090 | 30.00 | 1.280 | 1.820 | 5380 | 5910
8 | 8 | 0.500 | 16.12 | 18.96 | 103.5 | 152.3 | 1.04 | 7740 | 24.70 | 1.260 | 1.310 | 6890 | 7550
9 | 9 | 0.625 | 20.04 | 23.57 | 162.3 | 240.1 | 0.83 | 9060 | 21.60 | 1.370 | 1.140 | 7740 | 8450
10 | 10 | 0.625 | 23.50 | 27.64 | 255.6 | 362.4 | 0.71 | 10260 | 19.10 | 1.420 | 1.010 | 8610 | 9350
Notes:
1. Current ratings are based on 6101-T61 alloy with standard vent-holes in web. For 6101-T6 reduce the rating by 2 percent. Indoor ratings are based on 30°C rise over
40°C ambient in still but unconfined air, normally oxidized surface (e=0.35) and similarly for outdoor ratings, except 2 ft/sec cross wind (e=0.50). Horizontal mounting is
assumed with spacing sufficient to eliminate proximity effects, generally assumed to be 18-in. or over. For temperature rise of 50°C above 40°C ambient, the indoor ratings
for 30°C may be increased about 30 percent. Indoor ratings (D-C and A-C) calculated by computer and verified by test rounded. Outdoor ratings are calculations only.
2. For vent and notch arrangements, consult your AFL Sales Representative. The interior perimeter varies according to the washer diameters that are to be accommodated, and
as to their location per NEMA spacing. The 12 in. x 12 in. size is a opposite of two symmetric extrusions bolted together.
Stranded Copper Conductor
Size (AWG) | Stranding | Stranding Class | Weight (lbs/1000 ft) | Diameter (mils) |  | Hard Drawn |  | Medium-Hard Drawn |  | Soft-Drawn (Annealed) |  | Allowable Ampacity
|  |  |  | Individual Wires | Complete Conductor | Rated Strength (lbs) | DC Resistance (ohms/1000 ft) @20°C | Rated Strength (lbs) | DC Resistance (ohms/1000 ft) @20°C | Rated Strength (lbs) | DC Resistance (ohms/1000 ft) @20°C
STRANDED
1/0 | 7 | A. AA | 326.1 | 123 | 368 | 4752 | 1042 | 3705 | .1037 | 3221 | .1002 | 310
2/0 | 7 | A. AA | 410.9 | 138 | 414 | 5926 | 08267 | 4640 | .08224 | 4062 | 07949 | 355
2/0 | 19 | B | 410.9 | B4 | 418 | 5690 | 08267 | 4765 | .08224 | 4024 | 07949 | 355
3/0 | 7 | A. AA | 518.1 | 155 | 464 | 7366 | 06556 | 5812 | .06522 | 5118 | 06304 | 410
4/0 | 7 | A. AA | 553.3 | 174 | 522 | 9154 | 05199 | 7278 | .05172 | 5459 | 04999 | 480
4/0 | 19 | B | 553.3 | 106 | 528 | 9617 | 05199 | 7479 | .05172 | 5453 | 04999 | 480
250 | 19 | A | 771.9 | 115 | 574 | 11360 | 04400 | 8836 | .04378 | 7627 | 04231 | 530
250 | 37 | B | 771.9 | B2 | 575 | 11600 | 04400 | 8952 | .04378 | 7940 | 04231 | 530
300 | 19 | A | 926.2 | 126 | 628 | 13510 | 03667 | 10530 | .03648 | 9160 | 03526 | 590
350 | 19 | A | 1080.6 | 136 | 679 | 15590 | 03143 | 12200 | .03127 | 10680 | 03022 | 650
500 | 37 | AB | 1543.8 | 116 | 814 | 22510 | 02200 | 17550 | .02189 | 15240 | 02116 | 810
600 | 37 | AAA | 1852.5 | 127 | 891 | 27020 | 01834 | 21060 | .01825 | 18300 | 01763 | 910
750 | 61 | AB | 2315.6 | 111 | 998 | 34090 | 01467 | 26510 | .01459 | 22890 | 01410 | 1040
1000 | 61 | AB | 3087.5 | 128 | 1152 | 45030 | 01100 | 35100 | .01094 | 30500 | 01058 | 1240
■Ampacity based on 75*C conductor temperature; 25*C ambient temperature; 2 ft./sec. wind in sun.
Current Rating of Rectangular Aluminum Bus-Bar Arrangements
Amperes, for 6101-T61 Alloy 57% I ACS Conductivity (see footnotes!
Copper Pipe Bus
Nominal Size | Outside Diameter (Inches) | lnside Diameter (Inches) | CURRENT RATINGS IN AMPERES* |  |  |  | Size (Inches) | [] | 1 Bar | [][] | 2 Bars | [][][] | 3 Bars | [][][][] | 4 Bars
|  |  | 30° C Rise | 40° C Rise | 50° C Rise |  | ¼ X 1 | 308 |  | 601 |  | 887 |  | 1168
STANDARD PIPE SIZES | [6 empty] | 1½ | 429 |  | 817 |  | 1194 |  | 1561
1 | 1.315 | 1.062 | 850 | 975 | 1080 |  | 2 | 545 |  | 1021 |  | 1480 |  | 1915
1.5 | 1.9 | 1.6 | 1270 | 1445 | 1600 |  | 3 | 768 |  | 1410 |  | 2000 |  | 2530
2 | 2.375 | 2.062 | 1570 | 1780 | 1980 |  | 4 | 980 |  | 1760 |  | 2462 |  | 3081
2.5 | 2.875 | 2.5 | 1990 | 2275 | 2525 |  | 5 | 1184 |  | 2092 |  | 2905 |  | 3625
3 | 3.5 | 3.062 | 2540 | 2870 | 3225 |  | 6 | 1381 |  | 2413 |  | 3338 |  | 4146
3.5% | 4 | 3.5 | 3020 | 3465 | 3860 |  | 7 | 1760 |  | 3034 |  | 4183 |  | 5152
4 | 4.5 | 4 | 3365 | 3810 | 4305 |  | ⅜ X 2 | 678 |  | 1278 |  | 1831 |  | 2332
EXTRA HEAVY PIPE SIZES | [6 empty] | 3 | 941 |  | 1709 |  | 2384 |  | 2946
1 | 1.315 | 0.951 | 1000 | 1140 | 1255 |  | 4 | 1191 |  | 2099 |  | 2893 |  | 3574
1899-12-31 12:00 | 1.9 | 1.494 | 1445 | 1650 | 1830 |  | 5 | 1429 |  | 2483 |  | 3387 |  | 4178
2 | 2.375 | 1.933 | 1830 | 2080 | 2325 |  | 6 | 1657 |  | 2347 |  | 3857 |  | 4765
2.5 | 2.875 | 2.315 | 2365 | 2720 | 3020 |  | 8 | 2098 |  | 3569 |  | 4774 |  | 5875
3 | 3.5 | 2.892 | 2970 | 3365 | 3710 |  | 10 | 2534 |  | 4239 |  | 5632 |  | 6941
3.5 | 4 | 3.358 | 3380 | 3860 | 4255 |  | ½ X 3 | 1074 |  | 1991 |  | 2742 |  | 3297
4 | 4.5 | 3.818 | 3840 | 4350 | 4850 |  | 4 | 1369 |  | 2416 |  | 3264 |  | 3940
* 40°C Ambient, 98% Conductivity, 60Hz, 2fps horizontal wind | [6 empty] | 5 | 1634 |  | 2828 |  | 3778 |  | 4580
[7 empty] | 6 | 1892 |  | 3230 |  | 4284 |  | 5210
[7 empty] | 8 | 2393 |  | 4014 |  | 5276 |  | 6246
[7 empty] | 10 | 2880 |  | 4779 |  | 6256 |  | 7579
[7 empty] | Size (Inches) | [] | 1 Bar | [][] | 2 Bars | [][][] | 3 Bars | [][][][] | 4 Bars
[7 empty] | ¼ X 1 | 300 |  | 580 |  | 765 |  | 880
[7 empty] | 1½ | 416 |  | 785 |  | 1020 |  | 1180
[7 empty] | 2 | 530 |  | 980 |  | 1280 |  | 1460
[7 empty] | 3 | 735 |  | 1310 |  | 1700 |  | 1940
[7 empty] | 4 | 930 |  | 1600 |  | 2050 |  | 2330
[7 empty] | 5 | 1120 |  | 1830 |  | 2330 |  | 2610
[7 empty] | 6 | 1270 |  | 2010 |  | 2540 |  | 2800
[7 empty] | 7 | 1520 |  | 2320 |  | 2840 |  | 3080
[7 empty] | ⅜ X 2 | 660 |  | 1170 |  | 1490 |  | 1700
[7 empty] | 3 | 905 |  | 1550 |  | 1960 |  | 2220
[7 empty] | 4 | 1130 |  | 1860 |  | 2340 |  | 2630
[7 empty] | 5 | 1340 |  | 2110 |  | 2650 |  | 2940
[7 empty] | 6 | 1520 |  | 2330 |  | 2940 |  | 3200
[7 empty] | 8 | 1820 |  | 2700 |  | 3270 |  | 3490
[7 empty] | 10 | 1050 |  | 1650 |  | 2080 |  | 2340
[7 empty] | ½ X 3 | 1300 |  | 1960 |  | 2470 |  | 2750
[7 empty] | 5 | 1520 |  | 2240 |  | 2780 |  | 3090
[7 empty] | 6 | 1710 |  | 2490 |  | 3050 |  | 3330
[7 empty] | 8 | 2050 |  | 2900 |  | 3490 |  | 3720
Notes:
[7 empty] | 1 | Ratings based on 30°C rise over 40°C ambient in still but confined air (e=0.35), corresponding to usual indoor temperature. Vertical bar ampacity based on work by House and Tuttle. Horizontal bar ampacity from industry sources.
[7 empty] | 2 | Space between bars is assumed equal bar thickness.
[7 empty] | 3 | For ac phase spacings less than 18 inches an allowance for proximity effect must be made.
[7 empty] | 4 | Ratings are based on horizontal mounting, in air with no attachments.
Physical & Electrical Properties of Uniform-Thickness
Angle BUS Conductors - 6101-T6 alloy 55.0% lACS Conductivity (minimum)
Size (3) |  | Area sq in | Weight Ib/ft | Moment of Inertia in4 |  | Minimum Distance to Neutral Axis |  | Xa - 60 Hz Inductive Reactance 1 -ft Spacing microhms/ft | DC Resistance at 20°C microhms/ft | Rac/Rdc at 70°C 60 Hz | AC Resistance at 70°C 60Hz microhms/ft | AC Current Rating 60 Hz Amp (1)
W in | T in |  |  | lx or y | Iz | x or y | z |  |  |  |  | Indoor e=0.35 | Outdoor e=0.50
3 1/4 | 1/4 | 1.57 | 1.83 | 1.60 | 0.65 | 0.91 | 1.30 | 51.41 | 11.20 | 1.024 | 11.49 | 1300 | 1902
4 | 1/4 | 1.93 | 2.27 | 3.02 | 1.18 | 1.09 | 1.51 | 46.60 | 9.07 | 1.045 | 9.46 | 1550 | 2236
4 | 3/8 | 2.85 | 3.36 | 4.35 | 1.75 | 1.14 | 1.60 | 46.62 | 6.14 | 1.115 | 6.85 | 1850 | 2654
4 1/2 | 3/8 | 3.23 | 3.80 | 6.31 | 2.61 | 1.26 | 1.77 | 43.93 | 5.42 | 1.145 | 6.20 | 2050 | 2885
5 | 3/8 | 3.60 | 4.24 | 8.75 | 3.50 | 1.39 | 1.96 | 41.52 | 4.86 | 1.175 | 5.71 | 2250 | 3130
Notes:
1 | Indoor current ratings are based on 30°C rise over 40°C ambient in still but unconfined air, normally oxidized surface (e=0.35). Outdoor ratings are based similarly, but with 2 ft/sec crosswind (e=0.50). Horizontal mounting is assumed with spacing sufficient to eliminate proximity effects, generally assumed to be 18-in. or over. Indoor ratings based on work by House and Tuttle. Outdoor ratings from IEEE paper by Prager, Pemberton, Craig and Bleshman.
2 | Back-to-back angles are to be considered as separate members; not as a composite.
3 | Alignment grooves are extruded to facilitate centering of holes according to NEMA standard spacings.
4 | A modification of this design has a lug at top that does not interfere with bolting, yet it strengthens the shape against tendency to roll-over to the z-z axis in long spans subjected to large lateral short circuit forces. For equal weight of shape, the z-z radius of gyration is increased by 20 percent. The stress that causes roll-over is thereby increased about 40 percent.